# Load Shedding Guide Form Specification

Load Shed is a System consisting of one or more Load Shedding Controllers, an IEC61850-Ethernet network and IEC61850 capable end devices that provides infeed and load data & control, to re-establish power balance when infeed/loads balance is disrupted. Typically used at Industrial facilities with on-site generation.

# Load Shed Specifications

### Fast load shedding shall occur within 15 ms (with IEC61850-based communications) to avert destabilization of the electrical system due to a sudden loss of power source resulting in source/loads balance disruption.

### The Fast Load Shed system shall consist of: one or more Load shedding control devices, and IEC61850-Ethernet network, and end devices compliant to IEC 61850-8-1.

### The Fast Load Shedding Controller shall check if source/infeed lost exceeds remaining generation reserve per: Δ(Pgen) + Preserve ≥ 0 and shed enough load per pre-defined priorities (from low to high) above available generation reserve, ensuring optimal loads will be shed.

### Each source/infeed and load end device shall provide active power values to the Fast Load Shed Controller or Aggregator, and on-line status to the Fast Load Shed Controller via IEC61850 GOOSE. If IEC61850 GOOSE is not available in the end device, power values and on-line status shall be provided via Modbus protocol, Synchrophasors (IEEE C37.118 protocol & IEC61850-90-5), IEC 60870-5-101/104.

### The Fast Load Shed Controller shall issue the trip command to the load/load group end devices via IEC61850 digital GOOSE to achieve 15ms end-to-end operation (plus breaker time)

### At least 32 sources/infeeds and 128 loads/load Groups shall be supported.

### Each load/load Group shall have a load shedding priority (up to 128), and priority can be changed in real time while the system is operating from an HMI to the Load shedding Controller.

### The system shall be scalable to support over 1000 loads.

### The system shall be expandable by utilizing a Load shedding Controller with multiple aggregators, where each Aggregator shall aggregate up to 128 loads into up to 128 load groups.

### The Fast Load Shed Controller shall also facilitate secondary load shedding control to respond to system underfrequency, undervoltage, or overpower conditions.

# Hardware Specification

### The Fast Load Shed Controller hardware shall have as a minimum the following certifications: IEC 61850-3, IEEE 1613, CE, FCC Class A, UL, CCC.

### The Fast Load Shed Controller hardware shall have a fan-less design with no internal moving parts.

### Include as a minimum 8 Ethernet Gigabit Ports.

### Support at least 2 separate PRP and HSR Ethernet redundancy network cards.

### The Fast Load Shed Controller hardware design shall be able to simultaneously support non-Windows real-time operating system for the FLS application and a Windows Operating System for HMI application.

### The Fast Load Shed Controller shall have at least 70Gb storage capacity and 16Gb RAM.