D90Plus – Guide form Specification – OBSOLETE

## Release date: August 24th, 2007

## Revision Date: January 7th, 2019 (title changed to include ‘Obsolete’, footer updated)

Specification for Transmission Line Protection, Control and Monitoring

- Transmission line distance protection, control, monitoring and metering shall be supplied in one integrated digital (numerical) relay package for application on transmission lines and suitable for incorporation in an integrated substation control system.

- Applications shall include single-pole tripping, series-compensated lines and generator distance backup.

- The basic distance scheme without considering the carrier protection scheme shall have atleast three zones (zone1, zone2, zone 3) of high speed operating time up to trip impulse to the breaker (complete protection including the solid state trip relay operating time).

# Protection Functions

## Distance and Ground Distance Protection

- Individual measuring elements shall be provided for all phase and ground loops.

- Five zones of phase distance protection with memorized positive sequence voltage polarization, additional reactance, directional, and overcurrent supervision shall be included.

- Five zones of ground distance protection with memorized positive sequence voltage polarization, additional directional, overcurrent, and zero-sequence polarized (adaptive) reactance supervision, with Zones 2 through 5 augmented by an additional voltage polarized ground directional element.

- Distance characteristics for both phase and ground protection shall include mho, lens, and quadrilateral characteristics.

- All zones shall have independent direction, shape, reach, maximum torque angle, overcurrent supervision, zero-sequence compensation, blinders, and timer settings.

- All phase distance zones shall work with CTs and VTs located independently from each other at any side of a three-phase wye-delta transformer. Accurate reach and targeting shall be provided regardless of zone direction and location of the CTs and VTs.

- Zero-sequence compensation and mutual zero-sequence compensation shall be available for all ground distance zones. The compensating factors shall be provided as both magnitude and angle for each zone individually and independently.

- The distance elements shall include an adaptive reach feature for application on series compensated lines. The reach shall be adjusted automatically based on the current level to provide maximum security.

## Fast and Sensitive Ground Directional Protection

- The relay shall include neutral and negative-sequence directional overcurrent elements for fast and sensitive fault direction discrimination.

- The neutral and negative-Sequence elements shall include an offset impedance for faster and more reliable operation and application on series compensated lines.

- The neutral overcurrent element shall respond to neutral (internally calculated) or ground (externally supplied) current. The element shall respond to neutral (internally calculated) or auxiliary (externally supplied) polarizing voltage. The element shall be polarized from voltage, current or both.

- The negative-sequence directional element shall respond to negative-sequence direction and either negative-sequence or neutral currents.

- The neutral and negative-sequence directional elements shall include positive-sequence restraint for increased security.

- The neutral and negative-sequence directional elements shall include simultaneous forward and reverse indications.

- The neutral and negative-sequence directional elements shall be configurable for any pilot-aided scheme and for directional control of any protection element.

## Pilot-aided schemes

- Pilot-aided schemes shall include direct under reaching transfer trip (DUTT), permissive under reaching transfer trip (PUTT), permissive overreaching transfer trip (POTT), hybrid POTT , directional comparison blocking and unblocking scheme.

- The schemes shall include current reversal logic, permissive echo and provisions for weak-infeed applications.

- The schemes shall allow applying any protection element for directional and reach discrimination.

- The schemes shall allow applying any digital flag as a permission / blocking signal (RX). This shall include any input contact or any relay communications signal, or any combination of the above via programmable logic.

- The schemes shall allow interfacing their transmit signal (TX) via any input contact and/or relay communications signal.

## Overcurrent Protection

- Eight time overcurrent elements: for phase, neutral, ground and negative-sequence currents (two TOCs for each) shall be provided.

- Time overcurrent curve characteristics: IEEE, IEC, IAC, I2t, definite time, and four custom curves for precise coordination shall be available.

- Eight instantaneous overcurrent elements: for phase, neutral, ground and negative-sequence currents (two IOCs for each) shall be available.

- Six directional overcurrent elements: for phase, neutral, ground and negative-sequence (two elements for each) shall be available.

## Voltage Protection

- Two phase under- and one over-voltage elements shall be provided

- Additional Auxiliary under- and over-voltage elements shall be provided

- Neutral overvoltage element

- The voltage elements shall be time dependent.

## Out-of-Step Protection and Power Swing Blocking

- Integrated out-of-step tripping and power swing blocking functions shall be provided.

- The out-of-step tripping protection shall be programmable to trip either in an early (instantaneous) or delayed (when the current envelope is at the minimum) mode.

- Both out-of-step tripping and power swing blocking shall be programmable to work with 2 or 3 characteristics.

- Current supervision shall be available for both the functions.

## Load Encroachment

- Load encroachment characteristics responding to positive-sequence voltage and current shall be provided.

- Minimum voltage supervision shall be available for the function.

## Protection Programmable logics

- The relay shall have user programmable logic with necessary Boolean logic and control operators to define custom schemes. Flexible control of all input and output contacts shall be provided.

- The user programmable logics shall be executed at 1 msec execution rate.

- This user programmable logic shall be segregated from the user programmable automation logic if provided.

The relay shall provide functions to detect VT fuse failure and switch-on-to-fault (SOTF) protection

# Automation & Control Functions

## Two Breaker Failure Elements

- The breaker fail elements shall be configurable to respond to two different currents such as in breaker-and-a-half application.

- The breaker fail elements shall respond to three levels of current in three-pole and single-pole modes as well as to breaker contacts.

## Two Synchrocheck Elements

- The synchrocheck elements shall be configurable to respond to any combination of single-phase voltages such as in breaker-and-a-half application.

- Dead source logic shall be included.

## Automatic Recloser

- Four shot, three-pole/single-pole dual-breaker autorecloser shall be provided.

- The autorecloser shall allow one breaker to be out of service while the other breaker is in service.

- The autorecloser shall allow simultaneous or sequential reclosing of the two breakers.

- The autorecloser shall allow applying different dead-times for single-line-to-ground and multi-phase faults. This shall include a single-line-to-ground fault evolving into a multi-phase fault.

## Single-Pole Tripping

- Current and voltage-based phase selector shall be included.

- The relay shall allow any protection element to generate a trip command, which shall be supervised by the phase selector.

- Pilot-aided schemes with more than 1 bit of communications shall utilize both local and remote phase selection for accurate tripping on evolving and cross-country faults.

## Sixteen FlexElements™ for user-definable protection functions

- Flexible control of all input and output contacts shall be provided.

- All elements shall have a blocking input that allows supervision of the element from other elements, contact inputs, etc.

- The relay shall allow for peer-to-peer communications direct fiber or G.703 or RS422 interfaces.

## User Programmable Automation Logics

- The relay shall have user programmable automation logic with necessary Boolean logic and control operators to define custom schemes. Flexible control of all input and output contacts shall be provided.

- The user programmable automation logics shall provide a deterministic 50 msec execution rate.

- These user programmable automation logics shall be segregated from the user programmable protection.

## Switchable Setting Groups

- The relay shall have switch able setting groups for dynamic reconfiguration of the protection elements due to changed conditions such as system configuration changes, or seasonal requirements.

# Metering & Monitoring

- Voltage (phasors, true RMS values, symmetrical components), current (phasors, symmetrical components, true RMS values, harmonics up to 25th), real, reactive and apparent power, power factor, sensitive power, energy, demand and frequency.

- Data logger functionality shall be provided to profile operational data and stored in a non-volatile memory with up to 16 data logger channels with a user configurable sampling rate.

- The relay shall have breaker-monitoring capability including breaker arcing current (I2t, trip counter) and trip circuit monitoring capability

- The relay shall provide optional synchronized phasor information of voltage, current and sequence components according IEEEC37.118 standards. The streaming rate shall be user programmable, should have an onboard memory, manual or user configurable trigger options. The relay shall be capable of streaming the Synchrophasors data over its Ethernet port.

# Digital Fault Recorder (DFR)

The relay shall provide the following disturbance recording capability.

- Transient Recorder or Fast Scan Recorder: The relay shall have the capability to store raw sampled data with programmable sampling rate (max of 128 samples per cycle) with a provision for 64 records to store information about any physical I/O point or internal digital and analog quantities.

- Slow scan recorder or Disturbance Recorder: The relay shall have dedicated slow scan recorder, which can record 1 sample per cycle to 1 sample per min to record long-term events using internal digital and analog quantities.

- Sequence of Event recorder (SOE) function with a capacity to store at least 8000 events with 1ms time stamping accuracy.

# Relay HMI

The relay shall provide the following user interface capabilities.

- The relay shall provide a dedicated programmable annunciator screen in the front panel. The alarm labels shall be freely configurable with provisions to display them in multiple pages. The minimum number of characters per cell of the alarm page shall be 15.

- The relay also shall provide an optional human machine interface with pre-programmed display and control screens for the bay. The displays shall contain dedicated screens for metering, bay control, equipment manager, disturbance recorder and the status of the contacts of the I/O modules.

# Communications

- The relay’s communication option shall have dual IP redundancy or single IP redundancy Ethernet ports and shall support both fiber and copper ports in the same card at 100 Mbps.

- The relay shall support protocols DNP3.0, Modbus RTU, Modbus TCP/IP and IEC60870-5-104 and IEC61850 protocol.

- The IEC61850 protocol shall include all the relevant logical nodes for distance protection and configurable GOOSE and GSSE. The configurable GOOSE shall support transmitting analog quantities also using GOOSE messages

- The relay clock shall be capable of being synchronized with an IRIG-B signal to allow synchronism with other connected devices. The relay shall allow for SNTP network-based time synchronization.

# General Requirements

Contact outputs shall be trip rated Form-A with current and voltage circuit monitoring capability.  Hardware input/output capability shall be expandable.

The relay shall be supplied with supporting application software for use on a PC with Windows® operating systems. The program shall be capable of retrieving COMTRADE oscillography files from the relay to display, save, or print when troubleshooting. The software shall provide the capability of editing and managing settings files to store to the relay or disk backup, while on-line or off-line. The software shall also permit the updating of new relay firmware and viewing of all trip and alarm target messages.

Preference:

Manufacturer: GE Multilin

Device Number and Name: D90Plus, Line distance protection system