## Index
PQM Meter Modbus Maps | 1601-0493-A1 (GEK-134156) | About: This document contains all Modbus Maps for the products listed. For further communications information, see the corresponding manuals listed below. | Revision History
PQM Modbus Map | PQM Modbus Map | Manual: PQM Power Quality Meter Instruction Manual Manual 1665-0003-CJ (GEK-106296E) | A1
PQM Data Formats | PQM Data Formats | Manual: PQM Power Quality Meter Instruction Manual Manual 1665-0003-CJ (GEK-106296E) | A1
PQMII Modbus Map | PQMII Modbus Map | Manual: PQMII Power Quality Meter Communications Guide 1601-9090-A1 (GEK-113532) | A1
PQMII Data Formats | PQMII Data Formats | Manual: PQMII Power Quality Meter Communications Guide 1601-9090-A1 (GEK-113532) | A1

## PQM Modbus Map
GROUP | ADDR (HEX) | DESCRIPTION | RANGE | STEP VALUE | UNITS and SCALE | FORMAT | FACTORY DEFAULT
Notes:* Data type depends on the Command Operation Code.** Any valid Actual Values or Setpoints address. *** Maximum Setpoint value represents “OFF”.**** Minimum Setpoint value represents “OFF”. ***** Maximum Setpoint value represents “UNLIMITED”.****** Applicable to older revisions with VFD display only
Product Information (Input Registers) Addresses - 0000-007F
PRODUCT ID | 0 | Product Device Code | --- | --- | --- | F1 | 65
| 1 | Hardware Version Code | --- | --- | --- | F5 | current version
| 2 | Main Software Version Code | --- | --- | --- | F1 | current version
| 3 | Modification File Number 1 | --- | --- | --- | F1 | mod. file number 1
| 4 | Boot Software Version Code | --- | --- | --- | F1 | current version
| 5 | Supervisor Processor Version Code | --- | --- | --- | F1 | current version
| 6 | Product options | --- | --- | --- | F100 | from order code
| 7 | Modification File Number 2 | --- | --- | --- | F1 | mod. file number 2
| 8 | Modification File Number 3 | --- | --- | --- | F1 | mod. file number 3
| 9 | Modification File Number 4 | --- | --- | --- | F1 | mod. file number 4
| 000A | Modification File Number 5 | --- | --- | --- | F1 | mod. file number 5
| 000B | Reserved
| to | 
| 001F | Reserved
| 20 | Serial Number Character 1 and 2 | --- | --- | ASCII | F10 | 1st , 2nd char.
| 21 | Serial Number Character 3 and 4 | --- | --- | ASCII | F10 | 3rd, 4th char.
| 22 | Serial Number Character 5 and 6 | --- | --- | ASCII | F10 | 5th, 6th char
| 23 | Serial Number Character 7 and 8 | --- | --- | ASCII | F10 | 7th, 8th char.
| 24 | Reserved
| to | 
| 002F | Reserved
| 30 | Manufacture Month/Day | --- | --- | --- | F24 | manf. month/day
| 31 | Manufacture Year | --- | --- | --- | F25 | manufacture year
| 32 | Calibration Month/Day | --- | --- | --- | F24 | cal. month/day
| 33 | Calibration Year | --- | --- | --- | F25 | calibration year
| 34 | Reserved
| 35 | Reserved
| to | 
| 007F | Reserved
Commands (Holding Registers) Addresses - 0080-00EF
COMMANDS | 80 | Command Function Code | 5 | --- | --- | F1 | 5
| 81 | Command Operation Code | 1 to 35 | 1 | --- | F7 | 0
| 82 | Command Data 1 | 0 to 65535 | 1 | --- | * | 0
| 83 | Command Data 2 | 0 to 65535 | 1 | --- | F31 | 0
| 84 | Command Data 3 | 0 to 65535 | 1 | --- | F8 | 0
| 85 | Command Data 4 | 0 to 65535 | 1 | --- | F8 | 0
| 86 | Command Data 5 | 0 to 65535 | 1 | --- | F8 | 0
| 87 | Command Data 6 | 0 to 65535 | 1 | --- | F8 | 0
| 88 | Command Data 7 | 0 to 65535 | 1 | --- | F8 | 0
| 89 | Command Data 8 | 0 to 65535 | 1 | --- | F8 | 0
| 008A | Command Data 9 | 0 to 65535 | 1 | --- | F8 | 0
| 008B | Command Data 10 | 0 to 65535 | 1 | --- | F8 | 0
| 008C | Command Data 11 | 0 to 65535 | 1 | --- | F8 | 0
| 008D | Reserved
| to | 
| 00EF | Reserved
Broadcast Command (Holding Registers) Addresses - 00F0-00FF
BROADCAST COMMAND | 00F0 | Time Hours/Minutes | 0 to 65535 | 1 | hr/min | F22 | N/A
| 00F1 | Time Seconds | 0 to 59999 | 1 | ms | F23 | N/A
| 00F2 | Date Month/Day | 0 to 65535 | 1 | --- | F24 | N/A
| 00F3 | Date Year | 0 to 59999 | 1 | --- | F25 | N/A
| 00F4 | Reserved
| to | 
| 00FF | Reserved
User Definable Register (Input Registers) Addresses - 0100-017F
USER DEFINABLE REGISTERS | 100 | User Definable Data 0000 | --- | --- | --- | --- | ---
| 101 | User Definable Data 0001 | --- | --- | --- | --- | ---
| 102 | User Definable Data 0002 | --- | --- | --- | --- | ---
| 103 | User Definable Data 0003 | --- | --- | --- | --- | ---
| 104 | User Definable Data 0004 | --- | --- | --- | --- | ---
| 105 | User Definable Data 0005 | --- | --- | --- | --- | ---
| 106 | User Definable Data 0006 | --- | --- | --- | --- | ---
| 107 | User Definable Data 0007 | --- | --- | --- | --- | ---
| 108 | User Definable Data 0008 | --- | --- | --- | --- | ---
| 109 | User Definable Data 0009 | --- | --- | --- | --- | ---
| 010A | User Definable Data 000A | --- | --- | --- | --- | ---
| 010B | User Definable Data 000B | --- | --- | --- | --- | ---
| to |  |  |  |  |  | 
| 177 | User Definable Data 0077 | --- | --- | --- | --- | ---
| 178 | Reserved
| to | 
| 017F | Reserved
User Definable Register Index (Holding Registers) Addresses - 0180-01FF
USER DEFINABLE REGISTER INDEX | 180 | Register address for User Data 0000 | ** | 1 | --- | F1 | 0
| 181 | Register address for User Data 0001 | ** | 1 | --- | F1 | 0
| 182 | Register address for User Data 0002 | ** | 1 | --- | F1 | 0
| 183 | Register address for User Data 0003 | ** | 1 | --- | F1 | 0
| 184 | Register address for User Data 0004 | ** | 1 | --- | F1 | 0
| 185 | Register address for User Data 0005 | ** | 1 | --- | F1 | 0
| 186 | Register address for User Data 0006 | ** | 1 | --- | F1 | 0
| 187 | Register address for User Data 0007 | ** | 1 | --- | F1 | 0
| 188 | Register address for User Data 0008 | ** | 1 | --- | F1 | 0
| 189 | Register address for User Data 0009 | ** | 1 | --- | F1 | 0
| 018A | Register address for User Data 000A | ** | 1 | --- | F1 | 0
| 018B | Register address for User Data 000B | ** | 1 | --- | F1 | 0
| 018C | Register address for User Data 000C | ** | 1 | --- | F1 | 0
| 018D | Register address for User Data 000D | ** | 1 | --- | F1 | 0
| to |  |  |  |  |  | 
| 01F7 | Register address for User Data 0077 | ** | 1 | --- | F1 | 0
| 01F8 | Reserved
| to | 
| 01FF | Reserved
Actual Values (Input Registers) Addresses - 0200-0E1F
STATUS | 200 | Switch Input Status | --- | --- | --- | F101 | N/A
| 201 | LED Status Flags | --- | --- | --- | F102 | N/A
| 202 | LED Attribute Flags | --- | --- | --- | F103 | N/A
| 203 | Output Relay Status Flags | --- | --- | --- | F104 | N/A
| 204 | Alarm Active Status Flags 1 | --- | --- | --- | F105 | N/A
| 205 | Alarm Pickup Status Flags 1 | --- | --- | --- | F105 | N/A
| 206 | Alarm Active Status Flags 2 | --- | --- | --- | F106 | N/A
| 207 | Alarm Pickup Status Flags 2 | --- | --- | --- | F106 | N/A
| 208 | Alarm Active Status Flags 3 | --- | --- | --- | F107 | N/A
| 209 | Alarm Pickup Status Flags 3 | --- | --- | --- | F107 | N/A
| 020A | Aux. 1 Active Status Flags 1 | --- | --- | --- | F105 | N/A
| 020B | Aux. 1 Pickup Status Flags 1 | --- | --- | --- | F105 | N/A
| 020C | Aux. 1 Active Status Flags 2 | --- | --- | --- | F106 | N/A
| 020D | Aux. 1 Pickup Status Flags 2 | --- | --- | --- | F106 | N/A
| 020E | Aux. 1 Active Status Flags 3 | --- | --- | --- | F107 | N/A
| 020F | Aux. 1 Pickup Status Flags 3 | --- | --- | --- | F107 | N/A
| 210 | Aux. 2 Active Status Flags 1 | --- | --- | --- | F105 | N/A
| 211 | Aux. 2 Pickup Status Flags 1 | --- | --- | --- | F105 | N/A
| 212 | Aux. 2 Active Status Flags 2 | --- | --- | --- | F106 | N/A
| 213 | Aux. 2 Pickup Status Flags 2 | --- | --- | --- | F106 | N/A
| 214 | Aux. 2 Active Status Flags 3 | --- | --- | --- | F107 | N/A
| 215 | Aux. 2 Pickup Status Flags 3 | --- | --- | --- | F107 | N/A
| 216 | Aux. 3 Active Status Flags 1 | --- | --- | --- | F105 | N/A
| 217 | Aux. 3 Pickup Status Flags 1 | --- | --- | --- | F105 | N/A
| 218 | Aux. 3 Active Status Flags 2 | --- | --- | --- | F106 | N/A
| 219 | Aux. 3 Pickup Status Flags 2 | --- | --- | --- | F106 | N/A
| 021A | Aux. 3 Active Status Flags 3 | --- | --- | --- | F107 | N/A
| 021B | Aux. 3 Pickup Status Flags 3 | --- | --- | --- | F107 | N/A
| 021C | General Status | --- | --- | --- | F109 | N/A
| 021D | Encrypted Passcode | --- | --- | --- | F1 | N/A
| 021E | Reserved
| to |  |  |  |  |  | 
| 022F | Reserved
CLOCK | 230 | Time - Hours/Minutes | --- | --- | --- | F22 | N/A
| 231 | Time - Seconds | --- | --- | --- | F23 | N/A
| 232 | Time - Month/Day | --- | --- | --- | F24 | N/A
| 233 | Time Year | --- | --- | --- | F25 | N/A
| 234 | Reserved
| to |  |  |  |  |  | 
| 023F | Reserved
CURRENT | 240 | Phase A Current | --- | --- | A | F1 | N/A
| 241 | Phase B Current | --- | --- | A | F1 | N/A
| 242 | Phase C Current | --- | --- | A | F1 | N/A
| 243 | Average Current | --- | --- | A | F1 | N/A
| 244 | Neutral Current | --- | --- | A | F1 | N/A
| 245 | Current Unbalance | --- | --- | 0.1 x% | F1 | N/A
| 246 | Phase A Current - Minimum |  |  | A | F1 | N/A
| 247 | Phase B Current - Minimum |  |  | A | F1 | N/A
| 248 | Phase C Current - Minimum |  |  | A | F1 | N/A
| 249 | Neutral Current - Minimum |  |  | A | F1 | N/A
| 024A | Current Unbalance - Minimum |  |  | 0.1 x% | F1 | N/A
| 024B | Phase A Current - Maximum |  |  | A | F1 | N/A
| 024C | Phase B Current - Maximum |  |  | A | F1 | N/A
| 024D | Phase C Current - Maximum |  |  | A | F1 | N/A
| 024E | Neutral Current - Maximum |  |  | A | F1 | N/A
| 024F | Current Unbalance - Maximum |  |  | 0.1 x% | F1 | N/A
| 250 | Time - Hour/Minutes of Phase A Curr. Min | --- | --- | --- | F22 | N/A
| 251 | Time - Seconds of Phase A Current Min | --- | --- | --- | F23 | N/A
| 252 | Date - Month/Day of Phase A Current Min | --- | --- | --- | F24 | N/A
| 253 | Date - Year of Phase A Current Min | --- | --- | --- | F25 | N/A
| 254 | Time - Hour/Minutes of Phase B Curr. Min | --- | --- | --- | F22 | N/A
| 255 | Time - Seconds of Phase B Current Min | --- | --- | --- | F23 | N/A
| 256 | Date - Month/Day of Phase B Current Min | --- | --- | --- | F24 | N/A
| 257 | Date - Year of Phase B Current Min | --- | --- | --- | F25 | N/A
| 258 | Time - Hour/Minutes of Phase C Curr. Min | --- | --- | --- | F22 | N/A
| 259 | Time - Seconds of Phase C Current Min | --- | --- | --- | F23 | N/A
| 025A | Date - Month/Day of Phase C Current Min | --- | --- | --- | F24 | N/A
| 025B | Date - Year of Phase C Current Min | --- | --- | --- | F25 | N/A
| 025C | Time - Hour/Minutes of Neutral Current Min | --- | --- | --- | F22 | N/A
| 025D | Time - Seconds of Neutral Current Min | --- | --- | --- | F23 | N/A
| 025E | Date - Month/Day of Neutral Current Min | --- | --- | --- | F24 | N/A
| 025F | Date - Year of Neutral Current Min | --- | --- | --- | F25 | N/A
| 260 | Time - Hour/Minutes of Current Unbal. Min | --- | --- | --- | F22 | N/A
| 261 | Time - Seconds of Current Unbalance Min | --- | --- | --- | F23 | N/A
| 262 | Date - Month/Day of Current Unbal. Min | --- | --- | --- | F24 | N/A
| 263 | Date - Year of Current Unbalance Min | --- | --- | --- | F25 | N/A
| 264 | Time - Hour/Minutes of Phase A Curr. Max | --- | --- | --- | F22 | N/A
CURRENT continued | 265 | Time - Seconds of Phase A Current Max | --- | --- | --- | F23 | N/A
| 266 | Date - Month/Day of Phase A Current Max | --- | --- | --- | F24 | N/A
| 267 | Date - Year of Phase A Current Max | --- | --- | --- | F25 | N/A
| 268 | Time - Hour/Minutes of Phase B Curr. Max | --- | --- | --- | F22 | N/A
| 269 | Time - Seconds of Phase B Current Max | --- | --- | --- | F23 | N/A
| 026A | Date - Month/Day of Phase B Current Max | --- | --- | --- | F24 | N/A
| 026B | Date - Year of Phase B Current Max | --- | --- | --- | F25 | N/A
| 026C | Time - Hour/Minutes of Phase C Curr. Max | --- | --- | --- | F22 | N/A
| 026D | Time - Seconds of Phase C Current Max | --- | --- | --- | F23 | N/A
| 026E | Date - Month/Day of Phase C Current Max | --- | --- | --- | F24 | N/A
| 026F | Date - Year of Phase C Current Max | --- | --- | --- | F25 | N/A
| 270 | Time - Hour/Minutes of Neutral Current Max | --- | --- | --- | F22 | N/A
| 271 | Time - Seconds of Neutral Current Max | --- | --- | --- | F23 | N/A
| 272 | Date - Month/Day of Neutral Current Max | --- | --- | --- | F24 | N/A
| 273 | Date - Year of Neutral Current Max | --- | --- | --- | F25 | N/A
| 274 | Time - Hour/Minutes of Current Unbal. Max | --- | --- | --- | F22 | N/A
| 275 | Time - Seconds of Current Unbal. Max | --- | --- | --- | F23 | N/A
| 276 | Date - Month/Day of Current Unbal. Max | --- | --- | --- | F24 | N/A
| 277 | Date - Year of Current Unbalance Max | --- | --- | --- | F25 | N/A
| 278 | Reserved
| to |  |  |  |  |  | 
| 027F | Reserved
VOLTAGE | 0280 0281 | Voltage Van (High) Voltage Van (Low) | --- | --- | V | F3 | N/A
| 0282 0283 | Voltage Vbn (High) Voltage Vbn (Low) | --- | --- | V | F3 | N/A
| 0284 0285 | Voltage Vcn (High) Voltage Vcn (Low) | --- | --- | V | F3 | N/A
| 0286 0287 | Average Phase Voltage (High) Average Phase Voltage (Low) | --- | --- | V | F3 | N/A
| 0288 0289 | Voltage Vab (High) Voltage Vab (Low) | --- | --- | V | F3 | N/A
| 028A 028B | Voltage Vbc (High) Voltage Vbc (Low) | --- | --- | V | F3 | N/A
| 028C 028D | Voltage Vca (High) Voltage Vca (Low) | --- | --- | V | F3 | N/A
| 028E 028F | Average Line Voltage (High) Average Line Voltage (Low) | --- | --- | V | F3 | N/A
| 290 | Voltage Unbalance | --- | --- | 0.1 x % | F1 | N/A
| 0291 0292 | Voltage Van - Minimum (high) Voltage Van - Minimum (Low) | --- | --- | V | F3 | N/A
| 0293 0294 | Voltage Vbn - Minimum (high) Voltage Vbn - Minimum (Low) | --- | --- | V | F3 | N/A
| 0295 0296 | Voltage Vcn - Minimum (high) Voltage Vcn - Minimum (Low) | --- | --- | V | F3 | N/A
| 0297 0298 | Voltage Vab - Minimum (high) Voltage Vab - Minimum (Low) | --- | --- | V | F3 | N/A
| 0299 029A | Voltage Vbc - Minimum (high) Voltage Vbc - Minimum (Low) | --- | --- | V | F3 | N/A
| 029B 029C | Voltage Vca - Minimum (high) Voltage Vca - Minimum (Low) | --- | --- | V | F3 | N/A
| 029D | Voltage Unbalance - Minimum | --- | --- | 0.1 x% | F1 | N/A
| 029E 029F | Voltage Van - Maximum (high) Voltage Van - Maximum (Low) | --- | --- | V | F3 | N/A
| 02A0 02A1 | Voltage Vbn - Maximum (high) Voltage Vbn - Maximum (Low) | --- | --- | V | F3 | N/A
| 02A2 02A3 | Voltage Vcn - Maximum (high) Voltage Vcn - Maximum (Low) | --- | --- | V | F3 | N/A
| 02A4 02A5 | Voltage Vab - Maximum (high) Voltage Vab - Maximum (Low) | --- | --- | V | F3 | N/A
| 02A6 02A7 | Voltage Vbc - Maximum (high) Voltage Vbc - Maximum (Low) | --- | --- | V | F3 | N/A
| 02A8 02A9 | Voltage Vca - Maximum (high) Voltage Vca - Maximum (Low) | --- | --- | V | F3 | N/A
VOLTAGE continued | 02AA | Voltage Unbalance - Maximum | --- | --- | 0.1 x% | F1 | N/A
| 02AB | Time - Hour/Minutes of Voltage Van Min | --- | --- | --- | F22 | N/A
| 02AC | Time - Seconds of Voltage Van Min | --- | --- | --- | F23 | N/A
| 02AD | Date - Month/Day of Voltage Van Min | --- | --- | --- | F24 | N/A
| 02AE | Date - Year of Voltage Van Min | --- | --- | --- | F25 | N/A
| 02AF | Time - Hour/Minutes of Voltage Vbn Min | --- | --- | --- | F22 | N/A
| 02B0 | Time - Seconds of Voltage Vbn Min | --- | --- | --- | F23 | N/A
| 02B1 | Date - Month/Day of Voltage Vbn Min | --- | --- | --- | F24 | N/A
| 02B2 | Date - Year of Voltage Vbn Min | --- | --- | --- | F25 | N/A
| 02B3 | Time - Hour/Minutes of Voltage Vcn Min | --- | --- | --- | F22 | N/A
| 02B4 | Time - Seconds of Voltage Vcn Min | --- | --- | --- | F23 | N/A
| 02B5 | Date - Month/Day of Voltage Vcn Min | --- | --- | --- | F24 | N/A
| 02B6 | Date - Year of Voltage Vcn Min | --- | --- | --- | F25 | N/A
| 02B7 | Time - Hour/Minutes of Voltage Vab Min | --- | --- | --- | F22 | N/A
| 02B8 | Time - Seconds of Voltage Vab Min | --- | --- | --- | F23 | N/A
| 02B9 | Date - Month/Day of Voltage Vab Min | --- | --- | --- | F24 | N/A
| 02BA | Date - Year of Voltage Vab Min | --- | --- | --- | F25 | N/A
| 02BB | Time - Hour/Minutes of Voltage Vbc Min | --- | --- | --- | F22 | N/A
| 02BC | Time - Seconds of Voltage Vbc Min | --- | --- | --- | F23 | N/A
| 02BD | Date - Month/Day of Voltage Vbc Min | --- | --- | --- | F24 | N/A
| 02BE | Date - Year of Voltage Vbc Min | --- | --- | --- | F25 | N/A
| 02BF | Time - Hour/Minutes of Voltage Vca Min | --- | --- | --- | F22 | N/A
| 02C0 | Time - Seconds of Voltage Vca Min | --- | --- | --- | F23 | N/A
| 02C1 | Date - Month/Day of Voltage Vca Min | --- | --- | --- | F24 | N/A
| 02C2 | Date - Year of Voltage Vca Min | --- | --- | --- | F25 | N/A
| 02C3 | Time - Hour/Minutes of Voltage Unbal. Min | --- | --- | --- | F22 | N/A
| 02C4 | Time - Seconds of Voltage Unbalance Min | --- | --- | --- | F23 | N/A
| 02C5 | Date - Month/Day of Voltage Unbal. Min | --- | --- | --- | F24 | N/A
| 02C6 | Date - Year of Voltage Unbalance Min | --- | --- | --- | F25 | N/A
| 02C7 | Time - Hour/Minutes of Voltage Van Max | --- | --- | --- | F22 | N/A
| 02C8 | Time - Seconds of Voltage Van Max | --- | --- | --- | F23 | N/A
| 02C9 | Date - Month/Day of Voltage Van Max | --- | --- | --- | F24 | N/A
| 02CA | Date - Year of Voltage Van Max | --- | --- | --- | F25 | N/A
| 02CB | Time - Hour/Minutes of Voltage Vbn Max | --- | --- | --- | F22 | N/A
| 02CC | Time - Seconds of Voltage Vbn Max | --- | --- | --- | F23 | N/A
| 02CD | Date - Month/Day of Voltage Vbn Max | --- | --- | --- | F24 | N/A
| 02CE | Date - Year of Voltage Vbn Max | --- | --- | --- | F25 | N/A
| 02CF | Time - Hour/Minutes of Voltage Vcn Max | --- | --- | --- | F22 | N/A
| 02D0 | Time - Seconds of Voltage Vcn Max | --- | --- | --- | F23 | N/A
| 02D1 | Date - Month/Day of Voltage Vcn Max | --- | --- | --- | F24 | N/A
| 02D2 | Date - Year of Voltage Vcn Max | --- | --- | --- | F25 | N/A
| 02D3 | Time - Hour/Minutes of Voltage Vab Max | --- | --- | --- | F22 | N/A
VOLTAGE continued | 02D4 | Time - Seconds of Voltage Vab Max | --- | --- | --- | F23 | N/A
| 02D5 | Date - Month/Day of Voltage Vab Max | --- | --- | --- | F24 | N/A
| 02D6 | Date - Year of Voltage Vab Max | --- | --- | --- | F25 | N/A
| 02D7 | Time - Hour/Minutes of Voltage Vbc Max | --- | --- | --- | F22 | N/A
| 02D8 | Time - Seconds of Voltage Vbc Max | --- | --- | --- | F23 | N/A
| 02D9 | Date - Month/Day of Voltage Vbc Max | --- | --- | --- | F24 | N/A
| 02DA | Date - Year of Voltage Vbc Max | --- | --- | --- | F25 | N/A
| 02DB | Time - Hour/Minutes of Voltage Vca Max | --- | --- | --- | F22 | N/A
| 02DC | Time - Seconds of Voltage Vca Max | --- | --- | --- | F23 | N/A
| 02DD | Date - Month/Day of Voltage Vca Max | --- | --- | --- | F24 | N/A
| 02DE | Date - Year of Voltage Vca Max | --- | --- | --- | F25 | N/A
| 02DF | Time - Hour/Minutes of Voltage Unbal. Max | --- | --- | --- | F22 | N/A
| 2 | Time - Seconds of Voltage Unbalance Max | --- | --- | --- | F23 | N/A
| 20 | Date - Month/Day of Voltage Unbalance Max | --- | --- | --- | F24 | N/A
| 200 | Date - Year of Voltage Unbalance Max | --- | --- | --- | F25 | N/A
| 2000 | Reserved
| 20000 | Reserved
| 200000 | Reserved
| 02D6 | Reserved
| 20000000 | Va Phasor Angle | --- | --- | ° lag | F1
| 200000000 | Vb Phasor Angle | --- | --- | ° lag | F1
| 2000000000 | Vc Phasor Angle | --- | --- | ° lag | F1
| 02EA | Ia Phasor Angle | --- | --- | ° lag | F1
| 02EB | Ib Phasor Angle | --- | --- | ° lag | F1
| 02EC | Ic Phasor Angle | --- | --- | ° lag | F1
| 02ED | Reserved
| 02EE | Reserved
| 02EF | Reserved
POWER | 02F0 02F1 | 3 Phase Real Power (high) 3 Phase Real Power (low) | --- | --- | 0.01 x kW | F4 | N/A
| 02F2 02F3 | 3 Phase Reactive Power (high) 3 Phase Reactive Power (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 02F4 02F5 | 3 Phase Apparent Power (high) 3 Phase Apparent Power (low) | --- | --- | 0.01 x kVA | F3 | N/A
| 02F6 | 3 Phase Power Factor | --- | --- | 0.01 x PF | F2 | N/A
| 02F7 02F8 | Phase A Real Power (high) Phase A Real Power (low) | --- | --- | 0.01 x kW | F4 | N/A
| 02F9 02FA | Phase A Reactive Power (high) Phase A Reactive Power (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 02FB 02FC | Phase A Apparent Power (high) Phase A Apparent Power (low) | --- | --- | 0.01 x kVA | F3 | N/A
| 02FD | Phase A Power Factor | --- | --- | 0.01 x PF | F2 | N/A
| 02FE 02FF | Phase B Real Power (high) Phase B Real Power (low) | -- | --- | 0.01 x kW | F4 | N/A
| 0300 0301 | Phase B Reactive Power (high) Phase B Reactive Power (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 0302 0303 | Phase B Apparent Power (high) Phase B Apparent Power (low) | --- | --- | 0.01 x kVA | F3 | N/A
| 304 | Phase B Power Factor | --- | --- | 0.01 x PF | F2 | N/A
| 0305 0306 | Phase C Real Power (high) Phase C Real Power (low) | --- | --- | 0.01 x kW | F4 | N/A
| 0307 0308 | Phase C Reactive Power (high) Phase C Reactive Power (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 0309 030A | Phase C Apparent Power (high) Phase C Apparent Power (low) | --- | --- | 0.01 x kVA | F3 | N/A
| 030B | Phase C Power Factor | --- | --- | 0.01 x PF | F2 | N/A
| 030C 030D | 3 Phase Real Power - Minimum (high) 3 Phase Real Power - Minimum (low) | --- | --- | 0.01 x kW | F4 | N/A
| 030E 030F | 3 Phase Reactive Power - Minimum (high) 3 Phase Reactive Power - Minimum (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 0310 0311 | 3 Phase Apparent Power - Minimum (high) 3 Phase Apparent Power - Minimum (low) | --- | --- | 0.01 x kVA | F3 | N/A
| 312 | 3 Phase Power Factor - Minimum | --- | --- | 0.01 x PF | F2 | N/A
| 0313 0314 | 3 Phase Real Power - Maximum (high) 3 Phase Real Power - Maximum (low) | --- | --- | 0.01 x kW | F4 | N/A
| 0315 0316 | 3 Phase Reactive Power - Maximum (high) 3 Phase Reactive Power - Maximum (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 0317 0318 | 3 Phase Apparent Power - Maximum (high) 3 Phase Apparent Power - Maximum (low) | --- | --- | 0.01 x kVA | F3 | N/A
| 319 | 3 Phase Power Factor - Maximum | --- | --- | 0.01 x PF | F2 | N/A
POWER continued | 031A 031B | Phase A Real Power - Minimum (high) Phase A Real Power - Minimum (low) | --- | --- | 0.01 x kW | F4 | N/A
| 031C 031D | Phase A Reactive Power - Minimum (high) Phase A Reactive Power - Minimum (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 031E 031F | Phase A Apparent Power - Minimum (high) Phase A Apparent Power - Minimum (low) | --- | --- | 0.01 x kVA | F3 | N/A
| 320 | Phase A Power Factor - Minimum | --- | --- | 0.01 xPF | F2 | N/A
| 0321 0322 | Phase A Real Power - Maximum (high) Phase A Real Power - Maximum (low) | --- | --- | 0.01 x kW | F4 | N/A
| 0323 0324 | Phase A Reactive Power - Maximum (high) Phase A Reactive Power - Maximum (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 0325 0326 | Phase A Apparent Power - Maximum (high) Phase A Apparent Power - Maximum (low) | --- | --- | 0.01 x kVA | F3 | N/A
| 327 | Phase A Power Factor - Maximum | --- | --- | 0.01 x PF | F2 | N/A
| 0328 0329 | Phase B Real Power - Minimum (high) Phase B Real Power - Minimum (low) | --- | --- | 0.01 x kW | F4 | N/A
| 032A 032B | Phase B Reactive Power - Minimum (high) Phase B Reactive Power - Minimum (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 032C 032D | Phase B Apparent Power - Minimum (high) Phase B Apparent Power - Minimum (low) | --- | --- | 0.01 x kVA | F3 | N/A
| 032E | Phase B Power Factor - Minimum | --- | --- | 0.01 x PF | F2 | N/A
| 032F 0330 | Phase B Real Power - Maximum (high) Phase B Real Power - Maximum (low) | --- | --- | 0.01 x kW | F4 | N/A
| 0331 0332 | Phase B Reactive Power - Maximum (high) Phase B Reactive Power - Maximum (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 0333 0334 | Phase B Apparent Power - Maximum (high) Phase B Apparent Power - Maximum (low) | --- | --- | 0.01 x kVA | F3 | N/A
| 335 | Phase B Power Factor - Maximum | --- | --- | 0.01 x PF | F2 | N/A
| 0336 0337 | Phase C Real Power - Minimum (high) Phase C Real Power - Minimum (low) | --- | --- | 0.01 x kW | F4 | N/A
| 0338 0339 | Phase C Reactive Power - Minimum (high) Phase C Reactive Power - Minimum (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 033A 033B | Phase C Apparent Power - Minimum (high) Phase C Apparent Power - Minimum (low) | --- | --- | 0.01 x kVA | F3 | N/A
| 033C | Phase C Power Factor - Minimum | --- | --- | 0.01 x PF | F2 | N/A
| 033D 033E | Phase C Real Power - Maximum (high) Phase C Real Power - Maximum (low) | --- | --- | 0.01 x kW | F4 | N/A
| 033F 0340 | Phase C Reactive Power - Maximum (high) Phase C Reactive Power - Maximum (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 0341 0342 | Phase C Apparent Power - Maximum (high) Phase C Apparent Power - Maximum (low) | --- | --- | 0.01 x kVA | F3 | N/A
| 343 | Phase C Power Factor - Maximum | --- | --- | 0.01 x PF | F2 | N/A
| 344 | Time - Hour/Minutes of Real Power Min | --- | --- | --- | F22 | N/A
| 345 | Time - Seconds of Real Power Min | --- | --- | --- | F23 | N/A
| 346 | Date - Month/Day of Real Power Min | --- | --- | --- | F24 | N/A
| 347 | Date - Year of Real Power Min | --- | --- | --- | F25 | N/A
POWER continued | 348 | Time - Hour/Minutes of Reactive Pwr Min | --- | --- | --- | F22 | N/A
| 349 | Time - Seconds of Reactive Power Min | --- | --- | --- | F23 | N/A
| 034A | Date - Month/Day of Reactive Power Min | --- | --- | --- | F24 | N/A
| 034B | Date - Year of Reactive Power Min | --- | --- | --- | F25 | N/A
| 034C | Time - Hour/Minutes of Apparent Pwr Min | --- | --- | --- | F22 | N/A
| 034D | Time - Seconds of Apparent Power Min | --- | --- | --- | F23 | N/A
| 034E | Date - Month/Day of Apparent Power Min | --- | --- | --- | F24 | N/A
| 034F | Date - Year of Apparent Power Min | --- | --- | --- | F25 | N/A
| 350 | Time - Hour/Minutes of Power Factor Min | --- | --- | --- | F22 | N/A
| 351 | Time - Seconds of Power Factor Min | --- | --- | --- | F23 | N/A
| 352 | Date - Month/Day of Power Factor Min | --- | --- | --- | F24 | N/A
| 353 | Date - Year of Power Factor Min | --- | --- | --- | F25 | N/A
| 354 | Time - Hour/Minutes of Real Power Max | --- | --- | --- | F22 | N/A
| 355 | Time - Seconds of Real Power Max | --- | --- | --- | F23 | N/A
| 356 | Date - Month/Day of Real Power Max | --- | --- | --- | F24 | N/A
| 357 | Date - Year of Real Power Max | --- | --- | --- | F25 | N/A
| 358 | Time - Hour/Minutes of Reactive Pwr Max | --- | --- | --- | F22 | N/A
| 359 | Time - Seconds of Reactive Power Max | --- | --- | --- | F23 | N/A
| 035A | Date - Month/Day of Reactive Pwr Max | --- | --- | --- | F24 | N/A
| 035B | Date - Year of Reactive Power Max | --- | --- | --- | F25 | N/A
| 035C | Time - Hour/Minutes of Apparent Pwr Max | --- | --- | --- | F22 | N/A
| 035D | Time - Seconds of Apparent Pwr Max | --- | --- | --- | F23 | N/A
| 035E | Date - Month/Day of Apparent Pwr Max | --- | --- | --- | F24 | N/A
| 035F | Date - Year of Apparent Power Max | --- | --- | --- | F25 | N/A
| 360 | Time - Hour/Minutes of Power Factor Max | --- | --- | --- | F22 | N/A
| 361 | Time - Seconds of Power Factor Max | --- | --- | --- | F23 | N/A
| 362 | Date - Month/Day of Power Factor Max | --- | --- | --- | F24 | N/A
| 363 | Date - Year of Power Factor Max | --- | --- | --- | F25 | N/A
| 364 | Time - Hour/Min of Phase A Real Pwr Min | --- | --- | --- | F22 | N/A
| 365 | Time - Seconds of Phase A Real Pwr Min | --- | --- | --- | F23 | N/A
| 366 | Date - Month/Day of Phase A Real Pwr Min | --- | --- | --- | F24 | N/A
| 367 | Date - Year of Phase A Real Pwr Min | --- | --- | --- | F25 | N/A
| 368 | Time - Hour/Min of Phase A React Pwr Min | --- | --- | --- | F22 | N/A
| 369 | Time - Seconds of Phase A React Pwr Min | --- | --- | --- | F23 | N/A
| 036A | Date - Month/Day of Phase A React Pwr Min | --- | --- | --- | F24 | N/A
| 036B | Date - Year of Phase A Reactive Pwr Min | --- | --- | --- | F25 | N/A
| 036C | Time - Hour/Minutes of Phase A App Pwr Min | --- | --- | --- | F22 | N/A
| 036D | Time - Seconds of Phase A App Pwr Min | --- | --- | --- | F23 | N/A
| 036E | Date - Month/Day of Phase A App Pwr Min | --- | --- | --- | F24 | N/A
| 036F | Date - Year of Phase A Apparent Pwr Min | --- | --- | --- | F25 | N/A
POWER continued | 370 | Time - Hour/Minutes of Phase A PF Min | --- | --- | --- | F22 | N/A
| 371 | Time - Seconds of Phase A PF Min | --- | --- | --- | F23 | N/A
| 372 | Date - Month/Day of Phase A PF Min | --- | --- | --- | F24 | N/A
| 373 | Date - Year of Phase A Power Factor Min | --- | --- | --- | F25 | N/A
| 374 | Time - Hour/Min of Phase A Real Pwr Max | --- | --- | --- | F22 | N/A
| 375 | Time - Seconds of Phase A Real Pwr Max | --- | --- | --- | F23 | N/A
| 376 | Date - Month/Day of Phase A Real Pwr Max | --- | --- | --- | F24 | N/A
| 377 | Date - Year of Phase A Real Power Max | --- | --- | --- | F25 | N/A
| 378 | Time - Hour/Min of Phase A React Pwr Max | --- | --- | --- | F22 | N/A
| 379 | Time - Seconds of Phase A React Pwr Max | --- | --- | --- | F23 | N/A
| 037A | Date - Mnth/Day of Phase A React Pwr Max | --- | --- | --- | F24 | N/A
| 037B | Date - Year of Phase A Reactive Pwr Max | --- | --- | --- | F25 | N/A
| 037C | Time - Hour/Min of Phase A App Pwr Max | --- | --- | --- | F22 | N/A
| 037D | Time - Seconds of Phase A App Pwr Max | --- | --- | --- | F23 | N/A
| 037E | Date - Month/Day of Phase A App Pwr Max | --- | --- | --- | F24 | N/A
| 037F | Date - Year of Phase A Apparent Pwr Max | --- | --- | --- | F25 | N/A
| 380 | Time - Hour/Minutes of Phase A PF Max | --- | --- | --- | F22 | N/A
| 381 | Time - Seconds of Phase A PF Max | --- | --- | --- | F23 | N/A
| 382 | Date - Month/Day of Phase A PF Max | --- | --- | --- | F24 | N/A
| 383 | Date - Year of Phase A Power Factor Max | --- | --- | --- | F25 | N/A
| 384 | Time - Hour/Min of Phase B Real Pwr Min | --- | --- | --- | F22 | N/A
| 385 | Time - Seconds of Phase B Real Pwr Min | --- | --- | --- | F23 | N/A
| 386 | Date - Month/Day of Phase B Real Pwr Min | --- | --- | --- | F24 | N/A
| 387 | Date - Year of Phase B Real Power Min | --- | --- | --- | F25 | N/A
| 388 | Time - Hour/Min of Phase B React Pwr Min | --- | --- | --- | F22 | N/A
| 389 | Time - Seconds of Phase B React Pwr Min | --- | --- | --- | F23 | N/A
| 038A | Date - Month/Day of Phase B React Pwr Min | --- | --- | --- | F24 | N/A
| 038B | Date - Year of Phase B Reactive Pwr Min | --- | --- | --- | F25 | N/A
| 038C | Time - Hour/Min of Phase B App Pwr Min | --- | --- | --- | F22 | N/A
| 038D | Time - Seconds of Phase B App Pwr Min | --- | --- | --- | F23 | N/A
| 038E | Date - Month/Day of Phase B App Pwr Min | --- | --- | --- | F24 | N/A
| 038F | Date - Year of Phase B Apparent Pwr Min | --- | --- | --- | F25 | N/A
| 390 | Time - Hour/Minutes of Phase B PF Min | --- | --- | --- | F22 | N/A
| 391 | Time - Seconds of Phase B PF Min | --- | --- | --- | F23 | N/A
| 392 | Date - Month/Day of Phase B PF Min | --- | --- | --- | F24 | N/A
| 393 | Date - Year of Phase B PF Min | --- | --- | --- | F25 | N/A
| 394 | Time - Hour/Min of Phase B Real Pwr Max | --- | --- | --- | F22 | N/A
| 395 | Time - Seconds of Phase B Real Pwr Max | --- | --- | --- | F23 | N/A
| 396 | Date - Month/Day of Phase B Real Pwr Max | --- | --- | --- | F24 | N/A
| 397 | Date - Year of Phase B Real Power Max | --- | --- | --- | F25 | N/A
| 398 | Time - Hour/Min of Phase B React Pwr Max | --- | --- | --- | F22 | N/A
POWER continued | 399 | Time - Seconds of Phase B React Pwr Max | --- | --- | --- | F23 | N/A
| 039A | Date - Mnth/Day of Phase B React Pwr Max | --- | --- | --- | F24 | N/A
| 039B | Date - Year of Phase B Reactive Pwr Max | --- | --- | --- | F25 | N/A
| 039C | Time - Hour/Min of Phase B App Pwr Max | --- | --- | --- | F22 | N/A
| 039D | Time - Seconds of Phase B App Pwr Max | --- | --- | --- | F23 | N/A
| 039E | Date - Month/Day of Phase B App Pwr Max | --- | --- | --- | F24 | N/A
| 039F | Date - Year of Phase B Apparent Pwr Max | --- | --- | --- | F25 | N/A
| 03A0 | Time - Hour/Minutes of Phase B PF Max | --- | --- | --- | F22 | N/A
| 03A1 | Time - Seconds of Phase B PF Max | --- | --- | --- | F23 | N/A
| 03A2 | Date - Month/Day of Phase B PF Max | --- | --- | --- | F24 | N/A
| 03A3 | Date - Year of Phase B Power Factor Max | --- | --- | --- | F25 | N/A
| 03A4 | Time - Hour/Min of Phase C Real Pwr Min | --- | --- | --- | F22 | N/A
| 03A5 | Time - Seconds of Phase C Real Pwr Min | --- | --- | --- | F23 | N/A
| 03A6 | Date - Month/Day of Phase C Real Pwr Min | --- | --- | --- | F24 | N/A
| 03A7 | Date - Year of Phase C Real Power Min | --- | --- | --- | F25 | N/A
| 03A8 | Time - Hour/Min of Phase C React Pwr Min | --- | --- | --- | F22 | N/A
| 03A9 | Time - Seconds of Phase C React Pwr Min | --- | --- | --- | F23 | N/A
| 03AA | Date - Mnth/Day of Phase C React Pwr Min | --- | --- | --- | F24 | N/A
| 03AB | Date - Year of Phase C Reactive Pwr Min | --- | --- | --- | F25 | N/A
| 03AC | Time - Hour/Min of Phase C App Pwr Min | --- | --- | --- | F22 | N/A
| 03AD | Time - Seconds of Phase C App Pwr Min | --- | --- | --- | F23 | N/A
| 03AE | Date - Month/Day of Phase C App Pwr Min | --- | --- | --- | F24 | N/A
| 03AF | Date - Year of Phase C Apparent Pwr Min | --- | --- | --- | F25 | N/A
| 03B0 | Time - Hour/Minutes of Phase C PF Min | --- | --- | --- | F22 | N/A
| 03B1 | Time - Seconds of Phase C PF Min | --- | --- | --- | F23 | N/A
| 03B2 | Date - Month/Day of Phase C PF Min | --- | --- | --- | F24 | N/A
| 03B3 | Date - Year of Phase C Power Factor Min | --- | --- | --- | F25 | N/A
| 03B4 | Time - Hour/Min of Phase C Real Pwr Max | --- | --- | --- | F22 | N/A
| 03B5 | Time - Seconds of Phase C Real Pwr Max | --- | --- | --- | F23 | N/A
| 03B6 | Date - Month/Day of Phase C Real Pwr Max | --- | --- | --- | F24 | N/A
| 03B7 | Date - Year of Phase C Real Power Max | --- | --- | --- | F25 | N/A
| 03B8 | Time - Hour/Min of Phase C React Pwr Max | --- | --- | --- | F22 | N/A
| 03B9 | Time - Seconds of Phase C React Pwr Max | --- | --- | --- | F23 | N/A
| 03BA | Date - Mnth/Day of Phase C React Pwr Max | --- | --- | --- | F24 | N/A
| 03BB | Date - Year of Phase C Reactive Pwr Max | --- | --- | --- | F25 | N/A
| 03BC | Time - Hour/Min of Phase C App Pwr Max | --- | --- | --- | F22 | N/A
| 03BD | Time - Seconds of Phase C App Pwr Max | --- | --- | --- | F23 | N/A
| 03BE | Date - Month/Day of Phase C App Pwr Max | --- | --- | --- | F24 | N/A
| 03BF | Date - Year of Phase C Apparent Pwr Max | --- | --- | --- | F25 | N/A
| 03C0 | Time - Hour/Minutes of Phase C PF Max | --- | --- | --- | F22 | N/A
| 03C1 | Time - Seconds of Phase C PF Max | --- | --- | --- | F23 | N/A
POWER continued | 03C2 | Date - Month/Day of Phase C PF Max | --- | --- | --- | F24 | N/A
| 03C3 | Date - Year of Phase C Power Factor Max | --- | --- | --- | F25 | N/A
| 03C4 | Reserved
| to |  |  |  |  |  | 
| 03CF | Reserved
ENERGY | 03D0 03D1 | 3 Phase Positive Real Energy Used (high) 3 Phase Positive Real Energy Used (low) | --- | --- | kWh | F3 | N/A
| 03D2 03D3 | 3 Phase Negative Real Energy Used (high) 3 Phase Negative Real Energy Used (low) | --- | --- | kWh | F3 | N/A
| 03D4 03D5 | 3 Phase Positive React. Energy Used (high) 3 Phase Positive React. Energy Used (low) | --- | --- | kvarh | F3 | N/A
| 03D6 03D7 | 3 Phase Neg. React. Energy Used (high) 3 Phase Neg. React. Energy Used (low) | --- | --- | kvarh | F3 | N/A
| 03D8 03D9 | 3 Phase Apparent Energy Used (high) 3 Phase Apparent Energy Used (low) | --- | --- | kVAh | F3 | N/A
| 03DA 03DB | 3 Phase Energy Used in Last 24 h (high) 3 Phase Energy Used in Last 24 h (low) | --- | --- | kWh | F3 | N/A
| 03DC 03DD | 3 Phase Energy Cost Since Reset (high) 3 Phase Energy Cost Since Reset (low) | --- | --- | $ x 0.01 | F3 | N/A
| 03DE 03DF | 3 Phase Energy Cost Per Day (high) 3 Phase Energy Cost Per Day (low) | --- | --- | $ x 0.01 | F3 | N/A
| 3 | Time - Hours/Minutes of Last Reset | --- | --- | --- | F22 | N/A
| 30 | Time - Seconds of Last Reset | --- | --- | --- | F23 | N/A
| 300 | Date - Month/Day of Last Reset | --- | --- | --- | F24 | N/A
| 3000 | Date - Year of Last Reset | --- | --- | --- | F25 | N/A
| 03E4 03E5 | Tariff Period 1 Positive Real Energy (high) Tariff Period 1 Positive Real Energy (low) | --- | --- | kWh | F3 | N/A
| 03E6 03E7 | Tariff Period 1 Negative Real Energy (high) Tariff Period 1 Negative Real Energy (low) | --- | --- | kWh | F3 | N/A
| 03E8 03E9 | Tariff Period 2 Positive Real Energy (high) Tariff Period 2 Positive Real Energy (low) | --- | --- | kWh | F3 | N/A
| 03EA 03EB | Tariff Period 2 Negative Real Energy (high) Tariff Period 2 Negative Real Energy (low) | --- | --- | kWh | F3 | N/A
| 03EC 03ED | Tariff Period 3 Positive Real Energy (high) Tariff Period 3 Positive Real Energy (low) | --- | --- | kWh | F3 | N/A
| 03EE 03EF | Tariff Period 3 Negative Real Energy (high) Tariff Period 3 Negative Real Energy (low) | --- | --- | kWh | F3 | N/A
| 03F0 03F1 | Tariff Period 1 Cost (high) Tariff Period 1 Cost (low) | --- | --- | $ x 0.01 | F3 | N/A
| 03F2 03F3 | Tariff Period 2 Cost (high) Tariff Period 2 Cost (low) | --- | --- | $ x 0.01 | F3 | N/A
ENERGY continued | 03F4 03F5 | Tariff Period 3 Cost (high) Tariff Period 3 Cost (low) | --- | --- | $ x 0.01 | F3 | N/A
| 03F6 03F7 | Tariff Period 1 Net Energy Used (high) Tariff Period 1 Net Energy Used (low) | --- | --- | kWh | F3 | N/A
| 03F8 03F9 | Tariff Period 2 Net Energy Used (high) Tariff Period 2 Net Energy Used (low) | --- | --- | kWh | F3 | N/A
| 03FA 03FB | Tariff Period 3 Net Energy Used (high) Tariff Period 3 Net Energy Used (low) | --- | --- | kWh | F3 | N/A
| 03FC | Reserved
| to |  |  |  |  |  | 
| 03FF | Reserved
DEMAND | 400 | Phase A Current Demand | --- | --- | A | F1 | N/A
| 401 | Phase B Current Demand | --- | --- | A | F1 | N/A
| 402 | Phase C Current Demand | --- | --- | A | F1 | N/A
| 403 | Neutral Current Demand | --- | --- | A | F1 | N/A
| 0404 0405 | 3 Phase Real Power Demand (high) 3 Phase Real Power Demand (low) | --- | --- | 0.01 x kW | F4 | N/A
| 0406 0407 | 3 Phase React Power Demand (high) 3 Phase React Power Demand (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 0408 0409 | 3 Phase Apparent Power Demand (high) 3 Phase Apparent Power Demand (low) | --- | --- | 0.01 x kVA | F3 | N/A
| 040A | Phase A Current Demand - Maximum | --- | --- | A | F1 | N/A
| 040B | Phase B Current Demand - Maximum | --- | --- | A | F1 | N/A
| 040C | Phase C Current Demand - Maximum | --- | --- | A | F1 | N/A
| 040D | Neutral Current Demand - Maximum | --- | --- | A | F1 | N/A
| 040E 040F | 3 Phase Real Power Dmd (high) - Max 3 Phase Real Power Dmd (low) - Max | --- | --- | 0.01 x kW | F4 | N/A
| 0410 0411 | 3 Phase React Power Dmd (high) - Max 3 Phase React Power Dmd (low) - Max | --- | --- | 0.01 x kvar | F4 | N/A
| 0412 0413 | 3 Phase Apparent Power Dmd (high) - Max 3 Phase Apparent Power Dmd (low) - Max | --- | --- | 0.01 x kVA | F3 | N/A
| 414 | Time - Hours/Min of Phase A Cur. Dmd Max | --- | --- | --- | F22 | N/A
| 415 | Time - Seconds of Phase A Cur. Dmd Max | --- | --- | --- | F23 | N/A
| 416 | Date - Mnth/Day of Phase A Cur. Dmd Max | --- | --- | --- | F24 | N/A
| 417 | Date - Year of Phase A Cur. Dmd Max | --- | --- | --- | F25 | N/A
| 418 | Time - Hours/Min of Phase B Cur. Dmd Max | --- | --- | --- | F22 | N/A
| 419 | Time - Seconds of Phase B Cur. Dmd Max | --- | --- | --- | F23 | N/A
| 041A | Date - Mnth/Day of Phase B Cur. Dmd Max | --- | --- | --- | F24 | N/A
| 041B | Date - Year of Phase B Cur. Dmd Max | --- | --- | --- | F25 | N/A
| 041C | Time - Hours/Min of Phase C Cur. Dmd Max | --- | --- | --- | F22 | N/A
| 041D | Time - Seconds of Phase C Cur. Dmd Max | --- | --- | --- | F23 | N/A
| 041E | Date - Mnth/Day of Phase C Cur. Dmd Max | --- | --- | --- | F24 | N/A
| 041F | Date - Year of Phase C Cur. Dmd Max | --- | --- | --- | F25 | N/A
| 420 | Time - Hours/Min of Neutral Cur. Dmd Max | --- | --- | --- | F22 | N/A
| 421 | Time - Seconds of Neutral Cur. Dmd Max | --- | --- | --- | F23 | N/A
| 422 | Date - Month/Day of Neutral Cur. Dmd Max | --- | --- | --- | F24 | N/A
| 423 | Date - Year of Neutral Cur. Dmd Max | --- | --- | --- | F25 | N/A
| 424 | Time - Hours/Min of Real Pwr Dmd Max | --- | --- | --- | F22 | N/A
| 425 | Time - Seconds of Real Pwr Dmd Max | --- | --- | --- | F23 | N/A
| 426 | Date - Month/Day of Real Pwr Dmd Max | --- | --- | --- | F24 | N/A
| 427 | Date - Year of Real Pwr Dmd Max | --- | --- | --- | F25 | N/A
| 428 | Time - Hours/Min of React Pwr Dmd Max | --- | --- | --- | F22 | N/A
DEMAND continued | 429 | Time - Seconds of React Pwr Dmd Max | --- | --- | --- | F23 | N/A
| 042A | Date - Month/Day of React Pwr Dmd Max | --- | --- | --- | F24 | N/A
| 042B | Date - Year of React Pwr Dmd Max | --- | --- | --- | F25 | N/A
| 042C | Time - Hour/Min of App. Pwr Dmd Max | --- | --- | --- | F22 | N/A
| 042D | Time - Seconds of Apparent Pwr Dmd Max | --- | --- | --- | F23 | N/A
| 042E | Date - Month/Day of App. Pwr Dmd Max | --- | --- | --- | F24 | N/A
| 042F | Date - Year of Apparent Pwr Dmd Max | --- | --- | --- | F25 | N/A
| 430 | Reserved
| to |  |  |  |  |  | 
| 043F | Reserved
FREQUENCY | 440 | Frequency | --- | --- | 0.01 x Hz | F1 | N/A
| 441 | Frequency Minimum | --- | --- | 0.01 x Hz | F1 | N/A
| 442 | Frequency Maximum | --- | --- | 0.01 x Hz | F1 | N/A
| 443 | Time - Hours/Min of Frequency Max | --- | --- | --- | F22 | N/A
| 444 | Time - Seconds of Frequency Max | --- | --- | --- | F23 | N/A
| 445 | Date - Month/Day of Frequency Max | --- | --- | --- | F24 | N/A
| 446 | Date - Year of Frequency Max | --- | --- | --- | F25 | N/A
| 447 | Time - Hours/Min of Frequency Min | --- | --- | --- | F22 | N/A
| 448 | Time - Seconds of Frequency Min | --- | --- | --- | F23 | N/A
| 449 | Date - Month/Day of Frequency Min | --- | --- | --- | F24 | N/A
| 044A | Date - Year of Frequency Min | --- | --- | --- | F25 | N/A
| 044B | Reserved
| to |  |  |  |  |  | 
| 044F | Reserved
PULSE INPUT COUNTERS | 0450 0451 | Pulse Input 1 (high) Pulse Input 1 (low) | --- | --- | --- | F3 | N/A
| 0452 0453 | Pulse Input 2 (high) Pulse Input 2 (low) | --- | --- | --- | F3 | N/A
| 0454 0455 | Pulse Input 3 (high) Pulse Input 3 (low) | --- | --- | --- | F3 | N/A
| 0456 0457 | Pulse Input 4 (high) Pulse Input 4 (low) | --- | --- | --- | F3 | N/A
ANALOG INPUT | 0458 0459 | Main/Alternate Analog Input (High) Main/Alternate Analog Input (low) | --- | --- | --- | F3 | N/A
| 045A | Reserved
| to |  |  |  |  |  | 
| 045F | Reserved
PULSE INPUT COUNTERS | 0460 0461 | Totalized Pulse Input (high) Totalized Pulse Input (low) | --- | --- | --- | F3 | N/A
| 462 | Pulse Count Cleared Time – Hours/Min | --- | --- | --- | F22 | N/A
| 463 | Pulse Count Cleared Time – Seconds | --- | --- | --- | F23 | N/A
| 464 | Pulse Count Cleared Date – Month/Day | --- | --- | --- | F24 | N/A
| 465 | Pulse Count Cleared Date – Year | --- | --- | --- | F25 | N/A
| 466 | Reserved
| to |  |  |  |  |  | 
| 046F | Reserved
POWER QUALITY | 470 | Ia Crest Factor | --- | --- | 0.001 xCF | F1 | N/A
| 471 | Ib Crest Factor | --- | --- | 0.001 xCF | F1 | N/A
| 472 | Ic Crest Factor | --- | --- | 0.001 xCF | F1 | N/A
| 473 | Ia Transformer Harmonic Derating Factor | --- | --- | 0.01xTHDF | F1 | N/A
| 474 | Ib Transformer Harmonic Derating Factor | --- | --- | 0.01xTHDF | F1 | N/A
| 475 | Ic Transformer Harmonic Derating Factor | --- | --- | 0.01xTHDF | F1 | N/A
| 476 | Reserved
| 477 | Reserved
HARMONIC DISTORTION | 478 | Phase A Current THD | --- | --- | 0.1 x % | F1 | N/A
| 479 | Phase B Current THD | --- | --- | 0.1 x % | F1 | N/A
| 047A | Phase C Current THD | --- | --- | 0.1 x % | F1 | N/A
| 047B | Neutral Current THD | --- | --- | 0.1 x % | F1 | N/A
| 047C | Voltage Van THD | --- | --- | 0.1 x % | F1 | N/A
| 047D | Voltage Vbn THD | --- | --- | 0.1 x % | F1 | N/A
| 047E | Voltage Vcn THD | --- | --- | 0.1 x % | F1 | N/A
| 047F | Voltage Vab THD | --- | --- | 0.1 x % | F1 | N/A
| 480 | Voltage Vbc THD | --- | --- | 0.1 x % | F1 | N/A
| 481 | Reserved | --- | --- | 0.1 x % | F1 | N/A
| 482 | Phase A Current THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 483 | Phase B Current THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 484 | Phase C Current THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 485 | Neutral Current THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 486 | Voltage Van THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 487 | Voltage Vbn THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 488 | Voltage Vcn THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 489 | Voltage Vab THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 048A | Voltage Vbc THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 048B | Reserved | --- | --- | --- | --- | ---
| 048C | Time - Hour/Min of Phase A Cur. THD Max | --- | --- | --- | F22 | N/A
| 048D | Time - Seconds of Phase A Cur. THD Max | --- | --- | --- | F23 | N/A
| 048E | Date - Mnth/Day of Phase A Cur. THD Max | --- | --- | --- | F24 | N/A
| 048F | Date - Year of Phase A Cur. THD Max | --- | --- | --- | F25 | N/A
| 490 | Time - Hour/Min of Phase B Cur. THD Max | --- | --- | --- | F22 | N/A
| 491 | Time - Seconds of Phase B Cur. THD Max | --- | --- | --- | F23 | N/A
| 492 | Date - Mnth/Day of Phase B Cur. THD Max | --- | --- | --- | F24 | N/A
| 493 | Date - Year of Phase B Cur. THD Max | --- | --- | --- | F25 | N/A
| 494 | Time - Hour/Min of Phase C Cur. THD Max | --- | --- | --- | F22 | N/A
| 495 | Time - Seconds of Phase C Cur. THD Max | --- | --- | --- | F23 | N/A
| 496 | Date - Mnth/Day of Phase C Cur. THD Max | --- | --- | --- | F24 | N/A
| 497 | Date - Year of Phase C Cur. THD Max | --- | --- | --- | F25 | N/A
| 498 | Time - Hour/Min of Neutral Cur. THD Max | --- | --- | --- | F22 | N/A
HARMONIC DISTORTION continued | 499 | Time - Seconds of Neutral Cur. THD Max | --- | --- | --- | F23 | N/A
| 049A | Date - Mnth/Day of Neutral Cur. THD Max | --- | --- | --- | F24 | N/A
| 049B | Date - Year of Neutral Cur. THD Max | --- | --- | --- | F25 | N/A
| 049C | Time - Hours/Min of Van THD Max | --- | --- | --- | F22 | N/A
| 049D | Time - Seconds of Van THD Max | --- | --- | --- | F23 | N/A
| 049E | Date - Month/Day of Van THD Max | --- | --- | --- | F24 | N/A
| 049F | Date - Year of Van THD Max | --- | --- | --- | F25 | N/A
| 04A0 | Time - Hours/Min of Vbn THD Max | --- | --- | --- | F22 | N/A
| 04A1 | Time - Seconds of Vbn THD Max | --- | --- | --- | F23 | N/A
| 04A2 | Date - Month/Day of Vbn THD Max | --- | --- | --- | F24 | N/A
| 04A3 | Date - Year of Vbn THD Max | --- | --- | --- | F25 | N/A
| 04A4 | Time - Hours/Min of Vcn THD Max | --- | --- | --- | F22 | N/A
| 04A5 | Time - Seconds of Vcn THD Max | --- | --- | --- | F23 | N/A
| 04A6 | Date - Month/Day of Vcn THD Max | --- | --- | --- | F24 | N/A
| 04A7 | Date - Year of Vcn THD Max | --- | --- | --- | F25 | N/A
| 04A8 | Time - Hours/Min of Vab THD Max | --- | --- | --- | F22 | N/A
| 04A9 | Time - Seconds of Vab THD Max | --- | --- | --- | F23 | N/A
| 04AA | Date - Month/Day of Vab THD Max | --- | --- | --- | F24 | N/A
| 04AB | Date - Year of Vab THD Max | --- | --- | --- | F25 | N/A
| 04AC | Time - Hours/Min of Vbc THD Max | --- | --- | --- | F22 | N/A
| 04AD | Time - Seconds of Vbc THD Max | --- | --- | --- | F23 | N/A
| 04AE | Date - Month/Day of Vbc THD Max | --- | --- | --- | F24 | N/A
| 04AF | Date - Year of Vbc THD Max | --- | --- | --- | F25 | N/A
| 04B0 | Reserved
| 04B1 | Reserved
| 04B2 | Reserved
| 04B3 | Reserved
| 04B4 | Average Current THD | --- | --- | 0.1 x % | F1 | N/A
| 04B5 | Average Voltage THD | --- | --- | 0.1 x % | F1 | N/A
| 04B6 | Reserved
| to |  |  |  |  |  | 
| 04C7 | Reserved
DEBUG DATA | 04C8 | ADC Reference | --- | --- | --- | F1 | N/A
| 04C9 | Power Loss Fine Time | --- | --- | 10 ms | F1 | N/A
| 04CA | Power Loss Coarse Time | --- | --- | 0.1 min | F1 | N/A
| 04CB | Current Key Press | --- | --- | --- | F6 | N/A
| 04CC | Internal Fault Error Code | --- | --- | --- | F108 | N/A
| 04CD | Reserved
| to |  |  |  |  |  | 
| 04D7 | Reserved
MESSAGE BUFFER | 04D8 | Message Buffer characters 1 and 2 | --- | --- | ASCII | F10 | N/A
| 04D9 | Message Buffer characters 3 and 4 | --- | --- | ASCII | F10 | N/A
| 04DA | Message Buffer characters 5 and 6 | --- | --- | ASCII | F10 | N/A
| 04DB | Message Buffer characters 7 and 8 | --- | --- | ASCII | F10 | N/A
| 04DC | Message Buffer characters 9 and 10 | --- | --- | ASCII | F10 | N/A
| 04DD | Message Buffer characters 11 and 12 | --- | --- | ASCII | F10 | N/A
| 04DE | Message Buffer characters 13 and 14 | --- | --- | ASCII | F10 | N/A
| 04DF | Message Buffer characters 15 and 16 | --- | --- | ASCII | F10 | N/A
| 4 | Message Buffer characters 17 and 18 | --- | --- | ASCII | F10 | N/A
| 40 | Message Buffer characters 19 and 20 | --- | --- | ASCII | F10 | N/A
| 400 | Message Buffer characters 21 and 22 | --- | --- | ASCII | F10 | N/A
| 4000 | Message Buffer characters 23 and 24 | --- | --- | ASCII | F10 | N/A
| 40000 | Message Buffer characters 25 and 26 | --- | --- | ASCII | F10 | N/A
| 400000 | Message Buffer characters 27 and 28 | --- | --- | ASCII | F10 | N/A
| 4000000 | Message Buffer characters 29 and 30 | --- | --- | ASCII | F10 | N/A
| 40000000 | Message Buffer characters 31 and 32 | --- | --- | ASCII | F10 | N/A
| 400000000 | Message Buffer characters 33 and 34 | --- | --- | ASCII | F10 | N/A
| 4000000000 | Message Buffer characters 35 and 36 | --- | --- | ASCII | F10 | N/A
| 04EA | Message Buffer characters 37 and 38 | --- | --- | ASCII | F10 | N/A
| 04EB | Message Buffer characters 39 and 40 | --- | --- | ASCII | F10 | N/A
| 04EC | Reserved
| to |  |  |  |  |  | 
| 04F7 | Reserved
HIGH SPEED SAMPLES FOR HARMONIC SPECTRUM | 04F8 | High Speed Sampling Parameter | --- | --- | --- | F26 | N/A
| 04F9 04FA | High Speed Sampling Scale Factor (high) High Speed Sampling Scale Factor (low) | --- | --- | A or V x 10000 | F3 | N/A
| 04FB | Freq. of High Speed Sampling Waveform | --- | --- | 0.01 xHz | F1 | N/A
| 04FC | Time - Hours/Minutes of Last Sampling | --- | --- | --- | F22 | N/A
| 04FD | Time - Seconds of Last Sampling | --- | --- | --- | F23 | N/A
| 04FE | Date - Month/Day of Last Sampling | --- | --- | --- | F24 | N/A
| 04FF | Date - Year of Last Sampling | --- | --- | --- | F25 | N/A
| 500 | High Speed Sample Buffer 1 | --- | --- | ADC counts | F2 | N/A
| 501 | High Speed Sample Buffer 2 | --- | --- | ADC counts | F2 | N/A
| 502 | High Speed Sample Buffer 3 | --- | --- | ADC counts | F2 | N/A
| 503 | High Speed Sample Buffer 4 | --- | --- | ADC counts | F2 | N/A
| to |  |  |  |  |  | 
| 05FD | High Speed Sample Buffer 254 | --- | --- | ADC counts | F2 | N/A
| 05FE | High Speed Sample Buffer 255 | --- | --- | ADC counts | F2 | N/A
| 05FF | High Speed Sample Buffer 256 | --- | --- | ADC counts | F2 | N/A
| 600 | Reserved
| to |  |  |  |  |  | 
| 061F | Reserved
WAVEFORM CAPTURE HEADER | 620 | Time - Hours/Minutes of Last Capture | --- | --- | --- | F22 | N/A
| 621 | Time - Seconds of Last Capture | --- | --- | --- | F23 | N/A
| 622 | Date - Month/Day of Last Capture | --- | --- | --- | F24 | N/A
| 623 | Date - Year of Last Capture | --- | --- | --- | F25 | N/A
| 624 | Frequency of Last Capture | --- | --- | 0.01 x Hz | F1 | N/A
| 625 | Reserved
| 626 | Reserved
| 627 | Reserved
WAVEFORM CAPTURE Ia | 0628 0629 | Ia Waveform Capture Scale Factor (high) Ia Waveform Capture Scale Factor (low) | --- | --- | A x 10000 | F3 | N/A
| 062A | Ia Sample Buffer 1 | --- | --- | ADC counts | F2 | N/A
| 062B | Ia Sample Buffer 2 | --- | --- | ADC counts | F2 | N/A
| 062C | Ia Sample Buffer 3 | --- | --- | ADC counts | F2 | N/A
| 062D | Ia Sample Buffer 4 | --- | --- | ADC counts | F2 | N/A
| to |  |  |  |  |  | 
| 06A6 | Ia Sample Buffer 125 | --- | --- | ADC counts | F2 | N/A
| 06A7 | Ia Sample Buffer 126 | --- | --- | ADC counts | F2 | N/A
| 06A8 | Ia Sample Buffer 127 | --- | --- | ADC counts | F2 | N/A
| 06A9 | Ia Sample Buffer 128 | --- | --- | ADC counts | F2 | N/A
| 06AA | Reserved
| to |  |  |  |  |  | 
| 06AF | Reserved
WAVEFORM CAPTURE Ib | 06B0 06B1 | Ib Waveform Capture Scale Factor (high) Ib Waveform Capture Scale Factor (low) | --- | --- | A x 10000 | F3 | N/A
| 06B2 | Ib Sample Buffer 1 | --- | --- | ADC counts | F2 | N/A
| 06B3 | Ib Sample Buffer 2 | --- | --- | ADC counts | F2 | N/A
| 06B4 | Ib Sample Buffer 3 | --- | --- | ADC counts | F2 | N/A
| 06B5 | Ib Sample Buffer 4 | --- | --- | ADC counts | F2 | N/A
| to |  |  |  |  |  | 
| 072E | Ib Sample Buffer 125 | --- | --- | ADC counts | F2 | N/A
| 072F | Ib Sample Buffer 126 | --- | --- | ADC counts | F2 | N/A
| 730 | Ib Sample Buffer 127 | --- | --- | ADC counts | F2 | N/A
| 731 | Ib Sample Buffer 128 | --- | --- | ADC counts | F2 | N/A
| 732 | Reserved
| to |  |  |  |  |  | 
| 737 | Reserved
WAVEFORM CAPTURE Ic | 0738 0739 | Ic Waveform Capture Scale Factor (high) Ic Waveform Capture Scale Factor (low) | --- | --- | A x 10000 | F3 | N/A
| 073A | Ic Sample Buffer 1 | --- | --- | ADC counts | F2 | N/A
| 073B | Ic Sample Buffer 2 | --- | --- | ADC counts | F2 | N/A
| 073C | Ic Sample Buffer 3 | --- | --- | ADC counts | F2 | N/A
| 073D | Ic Sample Buffer 4 | --- | --- | ADC counts | F2 | N/A
| to |  |  |  |  |  | 
| 07B6 | Ic Sample Buffer 125 | --- | --- | ADC counts | F2 | N/A
| 07B7 | Ic Sample Buffer 126 | --- | --- | ADC counts | F2 | N/A
| 07B8 | Ic Sample Buffer 127 | --- | --- | ADC counts | F2 | N/A
| 07B9 | Ic Sample Buffer 128 | --- | --- | ADC counts | F2 | N/A
| 07BA | Reserved
| to |  |  |  |  |  | 
| 07BF | Reserved
WAVEFORM CAPTURE In | 07C0 07C1 | In Waveform Capture Scale Factor (high) In Waveform Capture Scale Factor (low) | --- | --- | A x 10000 | F3 | N/A
| 07C2 | In Sample Buffer 1 | --- | --- | ADC counts | F2 | N/A
| 07C3 | In Sample Buffer 2 | --- | --- | ADC counts | F2 | N/A
| 07C4 | In Sample Buffer 3 | --- | --- | ADC counts | F2 | N/A
| 07C5 | In Sample Buffer 4 | --- | --- | ADC counts | F2 | N/A
| to |  |  |  |  |  | 
| 083E | In Sample Buffer 125 | --- | --- | ADC counts | F2 | N/A
| 083F | In Sample Buffer 126 | --- | --- | ADC counts | F2 | N/A
| 840 | In Sample Buffer 127 | --- | --- | ADC counts | F2 | N/A
| 841 | In Sample Buffer 128 | --- | --- | ADC counts | F2 | N/A
| 842 | Reserved
| to |  |  |  |  |  | 
| 847 | Reserved
WAVEFORM CAPTURE Van | 0848 0849 | Van Waveform Capture Scale Factor (high) Van Waveform Capture Scale Factor (low) | --- | --- | V x 10000 | F3 | N/A
| 084A | Van Sample Buffer 1 | --- | --- | ADC counts | F2 | N/A
| 084B | Van Sample Buffer 2 | --- | --- | ADC counts | F2 | N/A
| 084C | Van Sample Buffer 3 | --- | --- | ADC counts | F2 | N/A
| 084D | Van Sample Buffer 4 | --- | --- | ADC counts | F2 | N/A
| to |  |  |  |  |  | 
| 08C6 | Van Sample Buffer 125 | --- | --- | ADC counts | F2 | N/A
| 08C7 | Van Sample Buffer 126 | --- | --- | ADC counts | F2 | N/A
| 08C8 | Van Sample Buffer 127 | --- | --- | ADC counts | F2 | N/A
| 08C9 | Van Sample Buffer 128 | --- | --- | ADC counts | F2 | N/A
| 08CA | Reserved
| to |  |  |  |  |  | 
| 08CF | Reserved
WAVEFORM CAPTURE Vbn | 08D0 08D1 | Vbn Waveform Capture Scale Factor (high) Vbn Waveform Capture Scale Factor (low) | --- | --- | V x 10000 | F3 | N/A
| 08D2 | Vbn Sample Buffer 1 | --- | --- | ADC counts | F2 | N/A
| 08D3 | Vbn Sample Buffer 2 | --- | --- | ADC counts | F2 | N/A
| 08D4 | Vbn Sample Buffer 3 | --- | --- | ADC counts | F2 | N/A
| 08D5 | Vbn Sample Buffer 4 | --- | --- | ADC counts | F2 | N/A
| to |  |  |  |  |  | 
| 094E | Vbn Sample Buffer 125 | --- | --- | ADC counts | F2 | N/A
| 094F | Vbn Sample Buffer 126 | --- | --- | ADC counts | F2 | N/A
| 950 | Vbn Sample Buffer 127 | --- | --- | ADC counts | F2 | N/A
| 951 | Vbn Sample Buffer 128 | --- | --- | ADC counts | F2 | N/A
| 952 | Reserved
| to |  |  |  |  |  | 
| 957 | Reserved
WAVEFORM CAPTURE Vcn | 0958 0959 | Vcn Waveform Capture Scale Factor (high) Vcn Waveform Capture Scale Factor (low) | --- | --- | V x 10000 | F3 | N/A
| 095A | Vcn Sample Buffer 1 | --- | --- | ADC counts | F2 | N/A
| 095B | Vcn Sample Buffer 2 | --- | --- | ADC counts | F2 | N/A
| 095C | Vcn Sample Buffer 3 | --- | --- | ADC counts | F2 | N/A
| 095D | Vcn Sample Buffer 4 | --- | --- | ADC counts | F2 | N/A
| to |  |  |  |  |  | 
| 09D6 | Vcn Sample Buffer 125 | --- | --- | ADC counts | F2 | N/A
| 09D7 | Vcn Sample Buffer 126 | --- | --- | ADC counts | F2 | N/A
| 09D8 | Vcn Sample Buffer 127 | --- | --- | ADC counts | F2 | N/A
| 09D9 | Vcn Sample Buffer 128 | --- | --- | ADC counts | F2 | N/A
| 09DA | Reserved
| to |  |  |  |  |  | 
| 09FF | Reserved
DATA LOGGER DATA | 0A00 | Data Log Memory Access Block Number | --- | --- | --- | F1 | 0
| 0A01 | Data Log Register 1 | --- | --- | --- | F1 | ---
| 0A02 | Data Log Register 2 | --- | --- | --- | F1 | ---
| 0A03 | Data Log Register 3 | --- | --- | --- | F1 | ---
| 0A04 | Data Log Register 4 | --- | --- | --- | F1 | ---
| to |  |  |  |  |  | 
| 0A3D | Data Log Register 61 | --- | --- | --- | F1 | ---
| 0A3E | Data Log Register 62 | --- | --- | --- | F1 | ---
| 0A3F | Data Log Register 63 | --- | --- | --- | F1 | ---
| 0A40 | Data Log Register 64 | --- | --- | --- | F1 | ---
| 0A41 | Reserved
| to |  |  |  |  |  | 
| 0A4F | Reserved
DATA LOGGER LOG NUMBERS | 0A50 | Ia Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A51 | Ib Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A52 | Ic Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A53 | Iavg Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A54 | In Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A55 | I Unbalance Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A56 | Van Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A57 | Vbn Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A58 | Vcn Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A59 | Vpavg Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A5A | Vab Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A5B | Vbc Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A5C | Vca Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A5D | Vlavg Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A5E | V Unbalance Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A5F | Pa Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A60 | Qa Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A61 | Sa Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A62 | PFa Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A63 | Pb Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A64 | Qb Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A65 | Sb Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A66 | PFb Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A67 | Pc Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A68 | Qc Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A69 | Sc Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A6A | PFc Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A6B | P3 Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A6C | Q3 Log Number | --- | --- | --- | F110 | 0 = not selected
DATA LOGGER LOG NUMBERS | 0A6D | S3 Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A6E | PF3 Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A6F | Frequency Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A70 | Positive kWh Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A71 | Negative kWh Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A72 | Positive kvarh Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A73 | Negative kvarh Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A74 | kVAh Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A75 | Ia Demand Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A76 | Ib Demand Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A77 | Ic Demand Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A78 | In Demand Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A79 | P3 Demand Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A7A | Q3 Demand Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A7B | S3 Demand Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A7C | Ia THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A7D | Ib THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A7E | Ic THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A7F | In THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A80 | Van THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A81 | Vbn THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A82 | Vcn THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A83 | Vab THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A84 | Vbc THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A85 | Analog Input Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A86 | Reserved
| to |  |  |  |  |  | 
| 0A8F | Reserved
DATA LOGGER LOG 1 HEADER | 0A90 0A91 | Log 1 Time Interval (high) Log 1 Time Interval (low) | --- | --- | s | F3 | N/A
| 0A92 | Log 1 Time - Hours/Minutes | --- | --- | --- | F22 | N/A
| 0A93 | Log 1 Time - Seconds | --- | --- | --- | F23 | N/A
| 0A94 | Log 1 Date - Month/Day | --- | --- | --- | F24 | N/A
| 0A95 | Log 1 Date - Year | --- | --- | --- | F25 | N/A
| 0A96 | Log 1 Start Address | --- | --- | --- | F1 | 0
| 0A97 | Log 1 Record Size | --- | --- | bytes | F1 | 0
| 0A98 | Log 1 Total Records | --- | --- | --- | F1 | 0
| 0A99 | Log 1 Pointer to First Item of First Record | --- | --- | --- | F1 | 0
| 0A9A | Log 1 Pointer to 1st Item of Record After Last | --- | --- | --- | F1 | 0
| 0A9B | Log 1 Status | --- | --- | --- | F35 | 0 = STOPPED
| 0A9C | Log 1 Records Used | --- | --- | --- | F1 | 0
| 0A9D 0A9E | Log 1 Time Until next Reading (high) Log 1 Time Until next Reading (low) | --- | --- | s | F3 | N/A
| 0A9F | Reserved
| to |  |  |  |  |  | 
| 0AA7 | Reserved
DATA LOGGER LOG 2 HEADER | 0AA8 | Log 2 Time Interval (high) | --- | --- | s | F3 | N/A
| 0AA9 | Log 2 Time Interval (low) | --- | --- | s | F3 | N/A
| 0AAA | Log 2 Time - Hours/Minutes | --- | --- | --- | F22 | N/A
| 0AAB | Log 2 Time - Seconds | --- | --- | --- | F23 | N/A
| 0AAC | Log 2 Date - Month/Day | --- | --- | --- | F24 | N/A
| 0AAD | Log 2 Date - Year | --- | --- | --- | F25 | N/A
| 0AAE | Log 2 Start Address | --- | --- | --- | F1 | 0
| 0AAF | Log 2 Record Size | --- | --- | bytes | F1 | 0
| 0AB0 | Log 2 Total Records | --- | --- | --- | F1 | 0
| 0AB1 | Log 2 Pointer to First Item of First Record | --- | --- | --- | F1 | 0
| 0AB2 | Log 2 Pointer to 1st Item of Record After Last | --- | --- | --- | F1 | 0
| 0AB3 | Log 2 Status | --- | --- | --- | F35 | 0 = STOPPED
| 0AB4 | Log 2 Records Used | --- | --- | --- | F1 | 0
| 0AB5 0AB6 | Log 2 Time Until next Reading (high) Log 2 Time Until next Reading (low) | --- | --- | s | F3 | N/A
| 0AB7 | Reserved
| to |  |  |  |  |  | 
| 0ACF | Reserved
EVENT RECORD | 0AD0 | Total Number of Events Since Last Clear | --- | --- | --- | F1 | 0
| 0AD1 | Event Record Last Cleared Time - Hrs./Min. | --- | --- | --- | F22 | N/A
| 0AD2 | Event Record Last Cleared Time - Seconds | --- | --- | --- | F23 | N/A
| 0AD3 | Event Record Last Cleared Date - Month/ Day | --- | --- | --- | F24 | N/A
| 0AD4 | Event Record Last Cleared Date - Year | --- | --- | --- | F25 | N/A
| 0AD5 | Reserved
| to |  |  |  |  |  | 
| 0ADF | Reserved
| 0AE0 | Record #N Event Number | --- | --- | --- | F1 | N/A
| 0AE1 | Record #N Event Cause | --- | --- | --- | F36 | 0 = NO EVENT
| 0AE2 | Record #N Time - Hours/Minutes | --- | --- | --- | F22 | N/A
| 0AE3 | Record #N Time - Seconds | --- | --- | --- | F23 | N/A
| 0AE4 | Record #N Date - Month/Day | --- | --- | --- | F24 | N/A
| 0AE5 | Record #N Date - Year | --- | --- | --- | F25 | N/A
| 0AE6 | Record #N Switches and Relays States | --- | --- | --- | F111 | N/A
| 0AE7 | Record #N Ia | --- | --- | A | F1 | N/A
| 0AE8 | Record #N Ib | --- | --- | A | F1 | N/A
| 0AE9 | Record #N Ic | --- | --- | A | F1 | N/A
| 0AEA | Record #N In | --- | --- | A | F1 | N/A
| 0AEB | Record #N I Unbalance | --- | --- | 0.1 x% | F1 | N/A
| 0AEC 0AED | Record #N Van (high) Record #N Van (low) | --- | --- | V | F3 | N/A
| 0AEE 0AEF | Record #N Vbn (high) Record #N Vbn (low) | --- | --- | V | F3 | N/A
| 0AF0 0AF1 | Record #N Vcn (high) Record #N Vcn (low) | --- | --- | V | F3 | N/A
| 0AF2 0AF3 | Record #N Vab (high) Record #N Vab (low) | --- | --- | V | F3 | N/A
| 0AF4 0AF5 | Record #N Vbc (high) Record #N Vbc (low) | --- | --- | V | F3 | N/A
| 0AF6 0AF7 | Record #N Vca (high) Record #N Vca (low) | --- | --- | V | F3 | N/A
| 0AF8 | Record #N V Unbalance | --- | --- | 0.1 x% | F1 | N/A
| 0AF9 0AFA | Record #N Pa (high) Record #N Pa (low) | --- | --- | 0.01 x kW | F4 | N/A
| 0AFB 0AFC | Record #N Qa (high) Record #N Qa (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 0AFD 0AFE | Record #N Sa (high) Record #N Sa (low) | --- | --- | 0.01 x kVA | F3 | N/A
EVENT RECORD continued | 0AFF | Record #N PFa | --- | --- | 0.01 x PF | F2 | N/A
| 0B00 0B01 | Record #N Pb (high) Record #N Pb (low) | --- | --- | 0.01 x kW | F4 | N/A
| 0B02 0B03 | Record #N Qb (high) Record #N Qb (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 0B04 0B05 | Record #N Sb (high) Record #N Sb (low) | --- | --- | 0.01 x kVA | F3 | N/A
| 0B06 | Record #N PFb | --- | --- | 0.01 x PF | F2 | N/A
| 0B07 0B08 | Record #N Pc (high) Record #N Pc (low) | --- | --- | 0.01 x kW | F4 | N/A
| 0B09 0B0A | Record #N Qc (high) Record #N Qc (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 0B0B 0B0C | Record #N Sc (high) Record #N Sc (low) | --- | --- | 0.01 x kVA | F3 | N/A
| 0B0D | Record #N PFc | --- | --- | 0.01 x PF | F2 | N/A
| 0B0E 0B0F | Record #N P3 (high) Record #N P3 (low) | --- | --- | 0.01 x kW | F4 | N/A
| 0B10 0B11 | Record #N Q3 (high) Record #N Q3 (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 0B12 0B13 | Record #N S3 (high) Record #N S3 (low) | --- | --- | 0.01 x kVA | F3 | N/A
| 0B14 | Record #N PF3 | --- | --- | 0.01 x PF | F2 | N/A
| 0B15 | Record #N Frequency | --- | --- | 0.01 x Hz | F1 | N/A
| 0B16 0B17 | Record #N Positive kWh (high) Record #N Positive kWh (low) | --- | --- | kWh | F3 | N/A
| 0B18 0B19 | Record #N Negative kWh (high) Record #N Negative kWh (low) | --- | --- | kWh | F3 | N/A
| 0B1A 0B1B | Record #N Positive kvarh (high) Record #N Positive kvarh (low) | --- | --- | kvarh | F3 | N/A
| 0B1C 0B1D | Record #N Negative kvarh (high) Record #N Negative kvarh (low) | --- | --- | kvarh | F3 | N/A
| 0B1E 0B1F | Record #N kVAh (high) Record #N kVAh (low) | --- | --- | kVAh | F3 | N/A
| 0B20 | Record #N Ia Demand | --- | --- | A | F1 | N/A
| 0B21 | Record #N Ib Demand | --- | --- | A | F1 | N/A
| 0B22 | Record #N Ic Demand | --- | --- | A | F1 | N/A
| 0B23 | Record #N In Demand | --- | --- | A | F1 | N/A
| 0B24 0B25 | Record #N P3 Demand (high) Record #N P3 Demand (low) | --- | --- | 0.01 x kW | F4 | N/A
| 0B26 0B27 | Record #N Q3 Demand (high) Record #N Q3 Demand (low) | --- | --- | 0.01 x kvar | F4 | N/A
| 0B28 0B29 | Record #N S3 Demand (high) Record #N S3 Demand (low) | --- | --- | 0.01 x kVA | F3 | N/A
EVENT RECORD continued | 0B2A | Record #N Ia THD | --- | --- | 0.1 x % | F1 | N/A
| 0B2B | Record #N Ib THD | --- | --- | 0.1 x % | F1 | N/A
| 0B2C | Record #N Ic THD | --- | --- | 0.1 x % | F1 | N/A
| 0B2D | Record #N In THD | --- | --- | 0.1 x % | F1 | N/A
| 0B2E | Record #N Van THD | --- | --- | 0.1 x % | F1 | N/A
| 0B2F | Record #N Vbn THD | --- | --- | 0.1 x % | F1 | N/A
| 0B30 | Record #N Vcn THD | --- | --- | 0.1 x % | F1 | N/A
| 0B31 | Record #N Vab THD | --- | --- | 0.1 x % | F1 | N/A
| 0B32 | Record #N Vbc THD | --- | --- | 0.1 x % | F1 | N/A
| 0B33 | Record #N Analog Input (high) | --- | --- | --- | F3 | N/A
| 0B34 | Record #N Analog Input (low) | --- | --- | --- | F3 | N/A
| 0B35 | Record #N Trace Memory Trigger Cause | --- | --- | --- | F41 | N/A
| 0B36 | Record #N Internal Fault Error Code | --- | --- | --- | F108 | N/A
| 0B37 | Reserved
| to |  |  |  |  |  | 
| 0B7F | Reserved
TRACE MEMORY | 0B80 | Trace Memory Usage | --- | --- | --- | F37 | N/A
| 0B81 | Trace Memory Trigger Flag | --- | --- | --- | F113 | N/A
| 0B82 | Trace Memory Trigger Counter | --- | --- | --- | F1 | N/A
| 0B83 | Total Trace Memory Triggers | --- | --- | --- | F1 | N/A
| 0B88 | Trigger Cause - Trace 1 | --- | --- | --- | F41 | N/A
| 0B89 | Time - Hours/Minutes - Trace 1 | --- | --- | --- | F22 | N/A
| 0B8A | Time - Seconds - Trace 1 | --- | --- | --- | F23 | N/A
| 0B8B | Date - Month/Day - Trace 1 | --- | --- | --- | F24 | N/A
| 0B8C | Date - Year - Trace 1 | --- | --- | --- | F25 | N/A
| 0B8D | Trigger Sample Number 1 | --- | --- | --- | F1 | N/A
| 0B8E | Frequency 1 | --- | --- | 0.01 x Hz | F1 | N/A
| 0B98 | Trigger Cause - Trace 2 | --- | --- | --- | F41 | N/A
| 0B99 | Time - Hours/Minutes - Trace 2 | --- | --- | --- | F22 | N/A
| 0B9A | Time - Seconds - Trace 2 | --- | --- | --- | F23 | N/A
| 0B9B | Date - Month/Day - Trace 2 | --- | --- | --- | F24 | N/A
| 0B9C | Date - Year - Trace 2 | --- | --- | --- | F25 | N/A
| 0B9D | Trigger Sample Number 2 | --- | --- | --- | F1 | N/A
| 0B9E | Frequency 2 | --- | --- | 0.01 x Hz | F1 | N/A
| 0BA8 | Trigger Cause - Trace 3 | --- | --- | --- | F41 | N/A
| 0BA9 | Time - Hours/Minutes - Trace 3 | --- | --- | --- | F22 | N/A
| 0BAA | Time - Seconds - Trace 3 | --- | --- | --- | F23 | N/A
| 0BAB | Date - Month/Day - Trace 3 | --- | --- | --- | F24 | N/A
| 0BAC | Date - Year - Trace 3 | --- | --- | --- | F25 | N/A
| 0BAD | Trigger Sample Number 3 | --- | --- | --- | F1 | N/A
| 0BAE | Frequency 3 | --- | --- | 0.01xHz | F1 | N/A
| 0BB8 | Trace Memory Waveform Selection | --- | --- | --- | F40 | N/A
| 0BB9 0BBA | Waveform Scale Factor (high) Waveform Scale Factor (low) | --- | --- | A/ Vx10000 | F3 | N/A
| 0BBB | Data Buffer 1 | --- | --- | ADCcount s/2 | F2 | N/A
| 0BBC | Data Buffer 2 | --- | --- | ADCcount s/2 | F2 | N/A
| to |  |  |  |  |  | 
| 0DF9 | Data Buffer 575 | --- | --- | ADCcount s/2 | F2 | N/A
| 0DFA | Data Buffer 576 | --- | --- | ADCcount s/2 | F2 | N/A
| 0DFB | Reserved
| to |  |  |  |  |  | 
| 0DFF | Reserved
| 0 | Invalid Serial Number Flag | --- | --- | --- | F117 | N/A
Setpoint Values (Holding Registers) Addresses - 1000-131F
METER ID | 1000 | Meter ID characters 1 and 2 | --- | --- | ASCII | F10 | N/A
| 1001 | Meter ID characters 3 and 4 | --- | --- | ASCII | F10 | N/A
| 1002 | Meter ID characters 5 and 6 | --- | --- | ASCII | F10 | N/A
| 1003 | Meter ID characters 7 and 8 | --- | --- | ASCII | F10 | N/A
| 1004 | Meter ID characters 9 and 10 | --- | --- | ASCII | F10 | N/A
| 1005 | Meter ID characters 11 and 12 | --- | --- | ASCII | F10 | N/A
| 1006 | Meter ID characters 13 and 14 | --- | --- | ASCII | F10 | N/A
| 1007 | Meter ID characters 15 and 16 | --- | --- | ASCII | F10 | N/A
| 1008 | Meter ID characters 17 and 18 | --- | --- | ASCII | F10 | N/A
| 1009 | Meter ID characters 19 and 20 | --- | --- | ASCII | F10 | N/A
| 100A | Reserved
| to |  |  |  |  |  | 
| 100F | Reserved
PREFERENCE S | 1010 | Default Message Time | 1 to 1201*** | 1 | min x0.1 | F1 | 10 = 1.0 min
| 1011 | Default Message Brightness ****** | 0 to 100 | 20 | % | F1 | 60%
| 1012 | Display Filter Constant | 1 to 10 | 1 | --- | F1 | 4
| 1013 | Reserved
| to |  |  |  |  |  | 
| 1017 | Reserved
RS485 COM1 SERIAL PORT | 1018 | Serial Communication Address | 1 to 255 | 1 | --- | F1 | 1
| 1019 | Modbus Baud Rate for RS485 COM1 | 0 to 4 | 1 | --- | F12 | 3 = 9600
| 101A | Parity for RS485 COM1 | 0 to 2 | 1 | --- | F13 | 0 = NONE
| 101B | Reserved
| to |  |  |  |  |  | 
| 101F | Reserved
RS485 COM2 SERIAL PORT | 1020 | Modbus Baud Rate for RS485 COM2 | 0 to 4 | 1 | --- | F12 | 3 = 9600
| 1021 | Parity for RS485 COM2 | 0 to 2 | 1 | --- | F13 | 0 = NONE
| 1022 | Reserved
| to |  |  |  |  |  | 
| 1027 | Reserved
RS232 SERIAL PORT | 1028 | Modbus Baud Rate for RS232 | 0 to 4 | 1 | --- | F12 | 3 = 9600
| 1029 | Parity for RS232 | 0 to 2 | 1 | --- | F13 | 0 = NONE
| 102A | Reserved
| to |  |  |  |  |  | 
| 102F | Reserved
CALCU- LATION PARAMETERS | 1030 | Current Demand Calculation Type | 0 to 2 | 1 | --- | F28 | 0 = Thermal Exponential
| 1031 | Current Demand Time Interval | 5 to 180 | 1 | minutes | F1 | 30 min
| 1032 | Power Demand Calculation Type | 0 to 2 | 1 | --- | F28 | 0 = Thermal Exponential
| 1033 | Power Demand Time Interval | 5 to 180 | 1 | minutes | F1 | 30 min
| 1034 | Energy Cost Per kWh | 1 to 50000 | 1 | ¢ x 0.01 | F1 | 10.00 ¢
| 1035 | Extract Fundamental | 0 to 1 | 1 | --- | F11 | 0=DISABLE
| 1036 | Reserved
| 1037 | Reserved
CLEAR DATA | 1038 | Clear Energy Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 1039 | Clear Max Demand Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 103A | Clear Min/Max Current Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 103B | Clear Min/Max Voltage Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 103C | Clear Min/Max Power Values | 0 to 1 | 1 | --- | F31 | 0 = NO
CLEAR DATA continued | 103D | Clear Max THD Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 103E | Clear Pulse Input Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 103F | Clear Event Record | 0 to 1 | 1 | --- | F31 | 0 = NO
| 1040 | Clear All Demand Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 1041 | Clear Frequency Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 1042 | Reserved
| 1043 | Reserved
DNP | 1044 | DNP Port | 0 to 3 | 1 | --- | F47 | 0 = NONE
| 1045 | DNP Slave Address | 0 to 255 | 1 | --- | F1 | 0
| 1046 | DNP Turnaround Time | 0 to 100 | 10 | ms | F1 | 10 ms
TARIFF | 1047 | Tariff Period 1 Start Time | 0 to 1439 | 1 | minutes | F1 | 0 min.
| 1048 | Tariff Period 1 Cost per kWh | 1 to 50000 | 1 | ¢  0.01 | F1 | 10.00 ¢
| 1049 | Tariff Period 2 Start Time | 0 to 1439 | 1 | minutes | F1 | 0 min.
| 104A | Tariff Period 2 Cost per kWh | 1 to 50000 | 1 | ¢  0.01 | F1 | 10.00 ¢
| 104B | Tariff Period 3 Start Time | 0 to 1439 | 1 | minutes | F1 | 0 min.
| 104C | Tariff Period 3 Cost per kWh | 1 to 50000 | 1 | ¢  0.01 | F1 | 10.00 ¢
| 104D | Reserved
| 104E | Reserved
| 104F | Reserved
CURRENT /VOLTAGE CONFIG. | 1050 | Phase CT Primary | 0 to 12000**** | 5 | A | F1 | 0 = OFF
| 1051 | Neutral Current Sensing | 0 to 2 | 1 | --- | F16 | 0 = OFF
| 1052 | Neutral CT Primary | 5 to 6000 | 5 | A | F1 | 100 A
| 1053 | VT Wiring | 0 to 6 | 1 | --- | F15 | 0 = OFF
| 1054 | VT Ratio | 10 to 35000 | 1 | 0.1 xratio | F1 | 1.0:1
| 1055 | VT Nominal Secondary Voltage | 40 to 600 | 1 | V | F1 | 120 V
| 1056 | Nominal Direct Input Voltage | 40 to 600 | 1 | V | F1 | 600 V
| 1057 | Nominal Frequency | 50 to 60 | 10 | Hz | F1 | 60 Hz
| 1058 | CT Wiring | 0 to 3 | 1 | --- | F44 | 0=A,B AND C
| 1059 | Reserved
| to |  |  |  |  |  | 
| 105F | Reserved
ANALOG OUTPUT 1 | 1060 | Analog Output 1 Main Type | 0 to 59 | 1 | --- | F14 | 5=Avg Ph Current
| 1061 | Analog Output 1 Main Min Value | See Analog Output Range Table on page –92 |  |  |  | 0
| 1062 | Analog Output 1 Main Max Value | See Analog Output Range Table on page –92 |  |  |  | 0
| 1063 | Analog Output 1 Alternate Type | 0 to 59 | 1 | --- | F14 | 0=NOT USED
| 1064 | Analog Output 1 Alternate Min Value | See Analog Output Range Table on page –92 |  |  |  | 0
| 1065 | Analog Output 1 Alternate Max Value | See Analog Output Range Table on page –92 |  |  |  | 0
| 1066 | Reserved
| 1067 | Analog Output 1 Serial Value |  | 1 | --- | F2 | 0
ANALOG OUTPUT 2 | 1068 | Analog Output 2 Main Type | 0 to 59 | 1 | --- | F14 | 18=3Ph Real Power
| 1069 | Analog Output 2 Main Min Value | See Analog Output Range Table on page –92 |  |  |  | 0
| 106A | Analog Output 2 Main Max Value | See Analog Output Range Table on page –92 |  |  |  | 0
| 106B | Analog Output 2 Alternate Type | 0 to 59 | 1 | --- | F14 | 0=NOT USED
| 106C | Analog Output 2 Alternate Min Value | See Analog Output Range Table on page –92 |  |  |  | 0
| 106D | Analog Output 2 Alternate Max Value | See Analog Output Range Table on page –92 |  |  |  | 0
| 106E | Reserved
| 106F | Analog Output 2 Serial Value |  | 1 | --- | F2 | 0
ANALOG OUTPUT 3 | 1070 | Analog Output 3 Main Type | 0 to 59 | 1 | --- | F14 | 19=3Ph Reactive Pwr
| 1071 | Analog Output 3 Main Min Value | See Analog Output Range Table on page –92
| 1072 | Analog Output 3 Main Max Value | See Analog Output Range Table on page –92
| 1073 | Analog Output 3 Alternate Type | 0 to 59 | 1 | --- | F14 | 0=NOT USED
| 1074 | Analog Output 3 Alternate Min Value | See Analog Output Range Table on page –92
| 1075 | Analog Output 3 Alternate Max Value | See Analog Output Range Table on page –92
| 1076 | Reserved
| 1077 | Analog Output 3 Serial Value |  | 1 | --- | F2 | 0
ANALOG OUTPUT 4 | 1078 | Analog Output 4 Main Type | 0 to 59 | 1 | --- | F14 | 17=3Ph Power Factor
| 1079 | Analog Output 4 Main Min Value | See Analog Output Range Table on page –92
| 107A | Analog Output 4 Main Max Value | See Analog Output Range Table on page –92
| 107B | Analog Output 4 Alternate Type | 0 to 59 | 1 | --- | F14 | 0=NOT USED
| 107C | Analog Output 4 Alternate Min Value | See Analog Output Range Table on page –92
| 107D | Analog Output 4 Alternate Max Value | See Analog Output Range Table on page –92
| 107E | Reserved
| 107F | Analog Output 4 Serial Value |  | 1 | --- | F2 | 0
ANALOG INPUT | 1080 | Analog Input Main/Alt Select Relay | 0 to 3 | 1 | --- | F19 | 0=OFF
| 1081 | Analog In Main Name 1st and 2nd char. | --- | --- | ASCII | F10 | ““
| 1082 | Analog In Main Name 3rd and 4th char. | --- | --- | ASCII | F10 | “MA”
| 1083 | Analog In Main Name 5th and 6th char. | --- | --- | ASCII | F10 | “IN”
| 1084 | Analog In Main Name 7th and 8th char. | --- | --- | ASCII | F10 | “ A”
| 1085 | Analog In Main Name 9th and 10th char. | -- | -- | ASCII | F10 | “NA”
| 1086 | Analog In Main Name 11th and 12th char. | -- | -- | ASCII | F10 | “LO”
| 1087 | Analog In Main Name 13th and 14th char. | --- | --- | ASCII | F10 | “G “
| 1088 | Analog In Main Name 15h and 16th char. | ---- | ---- | ASCII | F10 | “IN”
| 1089 | Analog In Main Name 17th and 18th char. | --- | --- | ASCII | F10 | “PU”
| 108A | Analog In Main Name 19th and 20th char. | --- | --- | ASCII | F10 | “T “
| 108B | Analog In Main Units 1st and 2nd char. | --- | --- | ASCII | F10 | “ U”
| 108C | Analog In Main Units 3rd and 4th char. | --- | --- | ASCII | F10 | “ni”
| 108D | Analog In Main Units 5th and 6th char. | --- | --- | ASCII | F10 | “ts”
| 108E | Analog In Main Units 7th and 8th char. | --- | --- | ASCII | F10 | “”
| 108F | Analog In Main Units 9th and 10th char. | --- | --- | ASCII | F10 | ““
| 1090 | Analog Input Main 4 mA Value | 0 to 65000 | 1 | --- | F1 | 0
| 1091 | Analog Input Main 20 mA Value | 0 to 65000 | 1 | --- | F1 | 0
| 1092 | Analog Input Main Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1093 | Analog Input Main Level | 0 to 65000 | 1 | --- | F1 | 0
| 1094 | Analog Input Main Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1095 | Reserved
| 1096 | Reserved
| 1097 | Reserved
| 1098 | Analog In Alt Name 1st and 2nd char. | --- | --- | ASCII | F10 | ““
| 1099 | Analog In Alt Name 3rd and 4th char. | --- | --- | ASCII | F10 | “AL”
| 109A | Analog In Alt Name 5th and 6th char. | --- | --- | ASCII | F10 | “T ”
| 109B | Analog In Alt Name 7th and 8th char. | --- | --- | ASCII | F10 | “ A”
| 109C | Analog In Alt Name 9th and 10th char. | -- | -- | ASCII | F10 | “NA”
| 109D | Analog In Alt Name 11th and 12th char. | -- | -- | ASCII | F10 | “LO”
| 109E | Analog In Alt Name 13th and 14th char. | --- | --- | ASCII | F10 | “G “
| 109F | Analog In Alt Name 15h and 16th char. | ---- | ---- | ASCII | F10 | “IN”
| 10A0 | Analog In Alt Name 17th and 18th char. | --- | --- | ASCII | F10 | “PU”
| 10A1 | Analog In Alt Name 19th and 20th char. | --- | --- | ASCII | F10 | “T “
| 10A2 | Analog In Alt Units 1st and 2nd char. | --- | --- | ASCII | F10 | “ U”
| 10A3 | Analog In Alt Units 3rd and 4th char. | --- | --- | ASCII | F10 | “ni”
| 10A4 | Analog In Alt Units 5th and 6th char. | --- | --- | ASCII | F10 | “ts”
| 10A5 | Analog In Alt Units 7th and 8th char. | --- | --- | ASCII | F10 | “”
| 10A6 | Analog In Alt Units 9th and 10th char. | --- | --- | ASCII | F10 | ““
| 10A7 | Analog Input Alt 4 mA Value | 0 to 65000 | 1 | --- | F1 | 0
| 10A8 | Analog Input Alt 20 mA Value | 0 to 65000 | 1 | --- | F1 | 0
ANALOG INPUT continued | 10A9 | Analog Input Alt Relay | 0-4 | 1 | --- | F29 | 0=OFF
| 10AA | Analog Input Alt Level | 0 to 65000 | 1 | --- | F1 | 0
| 10AB | Analog Input Alt Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 10AC | Reserved
| 10AD | Reserved
| 10AE | Reserved
| 10AF | Reserved
SWITCH A | 10B0 | Switch A Name characters 1 and 2 | --- | --- | ASCII | F10 | ““
| 10B1 | Switch A Name characters 3 and 4 | --- | --- | ASCII | F10 | “ S”
| 10B2 | Switch A Name characters 5 and 6 | --- | --- | ASCII | F10 | “WI”
| 10B3 | Switch A Name characters 7 and 8 | --- | --- | ASCII | F10 | “TC”
| 10B4 | Switch A Name characters 9 and 10 | --- | --- | ASCII | F10 | “H “
| 10B5 | Switch A Name characters 11 and 12 | --- | --- | ASCII | F10 | “IN“
| 10B6 | Switch A Name characters 13 and 14 | --- | --- | ASCII | F10 | “PU”
| 10B7 | Switch A Name characters 15 and 16 | --- | --- | ASCII | F10 | “T ”
| 10B8 | Switch A Name characters 17 and 18 | --- | --- | ASCII | F10 | “A “
| 10B9 | Switch A Name characters 19 and 20 | --- | --- | ASCII | F10 | ““
| 10BA | Switch A Function | 0 to 14 | 1 | --- | F20 | 0=NOT USED
| 10BB | Switch A Activation | 0 to 1 | 1 | --- | F27 | 1=CLOSED
| 10BC | Switch A Time Delay | 0 to 6000 | 1 | 0.1 x s | F1 | 0.0 s
| 10BD | Reserved
| 10BE | Reserved
| 10BF | Reserved
SWITCH B | 10C0 | Switch B Name characters 1 and 2 | --- | --- | ASCII | F10 | ““
| 10C1 | Switch B Name characters 3 and 4 | --- | --- | ASCII | F10 | “ S”
| 10C2 | Switch B Name characters 5 and 6 | --- | --- | ASCII | F10 | “WI”
| 10C3 | Switch B Name characters 7 and 8 | --- | --- | ASCII | F10 | “TC”
| 10C4 | Switch B Name characters 9 and 10 | --- | --- | ASCII | F10 | “H “
| 10C5 | Switch B Name characters 11 and 12 | --- | --- | ASCII | F10 | “IN“
| 10C6 | Switch B Name characters 13 and 14 | --- | --- | ASCII | F10 | “PU”
| 10C7 | Switch B Name characters 15 and 16 | --- | --- | ASCII | F10 | “T ”
| 10C8 | Switch B Name characters 17 and 18 | --- | --- | ASCII | F10 | “B “
| 10C9 | Switch B Name characters 19 and 20 | --- | --- | ASCII | F10 | ““
| 10CA | Switch B Function | 0 to 14 | 1 | --- | F20 | 0=NOT USED
| 10CB | Switch B Activation | 0 to 1 | 1 | --- | F27 | 1=CLOSED
| 10CC | Switch B Time Delay | 0 to 6000 | 1 | 0.1 x s | F1 | 0.0 s
| 10CD | Reserved
| 10CE | Reserved
| 10CF | Reserved
SWITCH C | 10D0 | Switch C Name characters 1 and 2 | --- | --- | ASCII | F10 | ““
| 10D1 | Switch C Name characters 3 and 4 | --- | --- | ASCII | F10 | “ S”
| 10D2 | Switch C Name characters 5 and 6 | --- | --- | ASCII | F10 | “WI”
| 10D3 | Switch C Name characters 7 and 8 | --- | --- | ASCII | F10 | “TC”
| 10D4 | Switch C Name characters 9 and 10 | --- | --- | ASCII | F10 | “H “
| 10D5 | Switch C Name characters 11 and 12 | --- | --- | ASCII | F10 | “IN“
| 10D6 | Switch C Name characters 13 and 14 | --- | --- | ASCII | F10 | “PU”
| 10D7 | Switch C Name characters 15 and 16 | --- | --- | ASCII | F10 | “T ”
| 10D8 | Switch C Name characters 17 and 18 | --- | --- | ASCII | F10 | “C “
| 10D9 | Switch C Name characters 19 and 20 | --- | --- | ASCII | F10 | ““
SWITCH C continued | 10DA | Switch C Function | 0 to 14 | 1 | --- | F20 | 0=NOT USED
| 10DB | Switch C Activation | 0 to 1 | 1 | --- | F27 | 1=CLOSED
| 10DC | Switch C Time Delay | 0 to 6000 | 1 | 0.1 x s | F1 | 0.0 s
| 10DD | Reserved
| 10DE | Reserved
| 10DF | Reserved
SWITCH D | 10E0 | Switch D Name characters 1 and 2 | --- | --- | ASCII | F10 | ““
| 10E1 | Switch D Name characters 3 and 4 | --- | --- | ASCII | F10 | “ S”
| 10E2 | Switch D Name characters 5 and 6 | --- | --- | ASCII | F10 | “WI”
| 10E3 | Switch D Name characters 7 and 8 | --- | --- | ASCII | F10 | “TC”
| 10E4 | Switch D Name characters 9 and 10 | --- | --- | ASCII | F10 | “H “
| 10E5 | Switch D Name characters 11 and 12 | --- | --- | ASCII | F10 | “IN“
| 10E6 | Switch D Name characters 13 and 14 | --- | --- | ASCII | F10 | “PU”
| 10E7 | Switch D Name characters 15 and 16 | --- | --- | ASCII | F10 | “T ”
| 10E8 | Switch D Name characters 17 and 18 | --- | --- | ASCII | F10 | “D “
| 10E9 | Switch D Name characters 19 and 20 | --- | --- | ASCII | F10 | ““
| 10EA | Switch D Function | 0 to 14 | 1 | --- | F20 | 0=NOT USED
| 10EB | Switch D Activation | 0 to 1 | 1 | --- | F27 | 1=CLOSED
| 10EC | Switch D Time Delay | 0 to 6000 | 1 | 0.1 x s | F1 | 0.0 s
| 10ED | Reserved
| 10EE | Reserved
| 10EF | Reserved
PULSE OUTPUT | 10F0 | Positive kWh Pulse Output Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 10F1 | Positive kWh Pulse Output Interval | 1 to 65000 | 1 | kWh | F1 | 100 kWh
| 10F2 | Negative kWh Pulse Output Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 10F3 | Negative kWh Pulse Output Interval | 1 to 65000 | 1 | kWh | F1 | 100 kWh
| 10F4 | Positive kvarh Pulse Output Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 10F5 | Positive kvarh Pulse Output Interval | 1 to 65000 | 1 | kvarh | F1 | 100 kvarh
| 10F6 | Negative kvarh Pulse Output Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 10F7 | Negative kvarh Pulse Output Interval | 1 to 65000 | 1 | kvarh | F1 | 100 kvarh
| 10F8 | kVAh Pulse Output Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 10F9 | kVAh Pulse Output Interval | 1 to 65000 | 1 | kVAh | F1 | 100 kVAh
| 10FA | Pulse Output Width | 100 to 2000 | 10 | ms | F1 | 100 ms
| 10FB | Serial Pulse Relay Interval | 100 to 10000 | 100 | ms | F1 | 100 ms
| 10FC | Reserved
PULSE INPUT | 10FD | Pulse Input Units 1st and 2nd char. | --- | --- | ASCII | F10 | “ U”
| 10FE | Pulse Input Units 3rd and 4th char. | --- | --- | ASCII | F10 | “ni”
| 10FF | Pulse Input Units 5th and 6th char. | --- | --- | ASCII | F10 | “ts”
| 1100 | Pulse Input Units 7th and 8th char. | --- | --- | ASCII | F10 | ““
| 1101 | Pulse Input Units 9th and 10th char. | --- | --- | ASCII | F10 | ““
| 1102 | Pulse Input 1 Value | 0 to 65000 | 1 | Units | F1 | 1
| 1103 | Pulse Input 2 Value | 0 to 65000 | 1 | Units | F1 | 1
| 1104 | Pulse Input 3 Value | 0 to 65000 | 1 | Units | F1 | 1
| 1105 | Pulse Input 4 Value | 0 to 65000 | 1 | Units | F1 | 1
| 1106 | Pulse Input Total | 0 to 10 | 1 | --- | F43 | 9 = 1+2+3+4
| 1107 | Reserved
ALARM RELAY | 1108 | Alarm Relay Operation | 0 to 1 | 1 | --- | F17 | 0 = NON- FAILSAFE
| 1109 | Alarm Relay Activation | 0 to 1 | 1 | --- | F18 | 0 = UNLATCHED
| 110A | Reserved
| to |  |  |  |  |  | 
| 110F | Reserved
AUXILIARY RELAY 1 | 1110 | Auxiliary Relay 1 Operation | 0 to 1 | 1 | --- | F17 | 0 = NON- FAILSAFE
| 1111 | Auxiliary Relay 1 Activation | 0 to 1 | 1 | --- | F18 | 0 = UNLATCHED
| 1112 | Reserved
| to |  |  |  |  |  | 
| 1117 | Reserved
AUXILIARY RELAY 2 | 1118 | Auxiliary Relay 2 Operation | 0 to 1 | 1 | --- | F17 | 0 = NON- FAILSAFE
| 1119 | Auxiliary Relay 2 Activation | 0 to 1 | 1 | --- | F18 | 0 = UNLATCHED
| 111A | Reserved
| to |  |  |  |  |  | 
| 111F | Reserved
AUXILIARY RELAY 3 | 1120 | Auxiliary Relay 3 Operation | 0 to 1 | 1 | --- | F17 | 0 = NON-FAILSAFE
| 1121 | Auxiliary Relay 3 Activation | 0 to 1 | 1 | --- | F18 | 0 = UNLATCHED
| 1122 | Reserved
| 1123 | Reserved
| 1124 | Reserved
| 1125 | Reserved
CURRENT/ VOLTAGE ALARMS | 1126 | Phase Overcurrent Activation | 0 to 1 | 1 | --- | F115 | 0=AVERAGE
| 1127 | Detect I/V Alarms Using Percentage | 0 to 1 | 1 | --- | F31 | 0=NO
| 1128 | Phase Undercurrent Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1129 | Phase Undercurrent Level in Amps | 1 to 12000 | 1 | A | F1 | 100 A
| 112A | Phase Undercurrent Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 112B | Phase Overcurrent Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 112C | Phase Overcurrent Level in Amps | 1 to 12000 | 1 | A | F1 | 100 A
| 112D | Phase Overcurrent Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 112E | Neutral Overcurrent Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 112F | Neutral Overcurrent Level in Amps | 1 to 12000 | 1 | A | F1 | 100 A
| 1130 | Neutral Overcurrent Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1131 | Undervoltage Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1132 | Undervoltage Level in Volts | 20 to 65000 | 1 | V | F1 | 100 V
| 1133 | Undervoltage Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1134 | Phases Req’d for Operation of U/V | 0 to 2 | 1 | --- | F30 | 0=ANY ONE
| 1135 | Detect U/V Below 20V | 0 to 1 | 1 | --- | F11 | 0=DISABLE
| 1136 | Overvoltage Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1137 | Overvoltage Level in Volts | 1 to 65000 | 1 | V | F1 | 100 V
| 1138 | Overvoltage Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1139 | Phases Req’d for Operation of O/V | 0 to 2 | 1 | --- | F30 | 0=ANY ONE
| 113A | Phase Current Unbalance Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 113B | Phase Current Unbalance Level | 1 to 100 | 1 | % | F1 | 10%
| 113C | Phase Current Unbalance Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 113D | Voltage Unbalance Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 113E | Voltage Unbalance Level | 1 to 100 | 1 | % | F1 | 10%
| 113F | Voltage Unbalance Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1140 | Voltage Phase Reversal Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1141 | Voltage Phase Reversal Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1142 | Detect Undercurrent When 0A | 0 to 1 | 1 | --- | F31 | 0=NO
| 1143 | Phase Undercurrent Level in % of CT | 1 to 100 | 1 | % | F1 | 100%
| 1144 | Phase Overcurrent Level in % of CT | 1 to 150 | 1 | % | F1 | 100%
| 1145 | Neutral Overcurrent Level in % of CT | 1 to 150 | 1 | % | F1 | 100%
| 1146 | Undervoltage Level in % of VT | 20 to 100 | 1 | % | F1 | 100%
| 1147 | Overvoltage Level in % of VT | 20 to 100 | 1 | % | F1 | 150%
TOTAL HARMONIC DISTORTION ALARMS | 1148 | Average Current THD Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1149 | Average Current THD Level | 5 to 1000 | 5 | 0.1 x % | F1 | 100=10.0%
| 114A | Average Current THD Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 114B | Average Voltage THD Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 114C | Average Voltage THD Level | 5 to 1000 | 5 | 0.1 x % | F1 | 100=10.0%
| 114D | Average Voltage THD Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 114E | Reserved
| to |  |  |  |  |  | 
| 1157 | Reserved
FREQUENCY ALARMS | 1158 | Underfrequency Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1059 | Underfrequency Level | 2000 to 7000 | 1 | 0.01 x Hz | F1 | 40.00 Hz
| 115A | Underfrequency Delay | 1 to 100 | 1 | 0.1 x s | F1 | 100=10.0 s
| 115B | Zero Frequency Detect | 0 to 1 | 1 | --- | F11 | 0=DISABLE
| 115C | Overfrequency Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 115D | Overfrequency Level | 2000 to 12500 | 1 | 0.01 x Hz | F1 | 70.00 Hz
| 115E | Overfrequency Delay | 1 to 100 | 1 | 0.1 x s | F1 | 100=10.0 s
| 115F | Reserved
| to |  |  |  |  |  | 
| 1166 | Reserved
POWER ALARMS | 1167 | Power Alarms Level Base Units | 0 to 1 | 1 | --- | F114 | 0=kW/kVAR
| 1168 | Positive Real Power Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1169 | Positive Real Power Level in kW | 1 to 65000 | 1 | kW | F1 | 1000 kW
| 116A | Positive Real Power Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 116B | Negative Real Power Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 116C | Negative Real Power Level in kW | 1 to 65000 | 1 | kW | F1 | 1000 kW
| 116D | Negative Real Power Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 116E | Positive Reactive Power Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 116F | Positive Reactive Power Level in kVAR | 1 to 65000 | 1 | kVAR | F1 | 1000 kVAR
| 1170 | Positive Reactive Power Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1171 | Negative Reactive Power Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1172 | Negative Reactive Power Level in kVAR | 1 to 65000 | 1 | kVAR | F1 | 1000 kVAR
| 1173 | Negative Reactive Power Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1174 | Positive Real Power Level in MW | 1 to 65000 | 1 | 0.01 MW | F1 | 10.00MW
| 1175 | Negative Real Power Level in MW | 1 to 65000 | 1 | 0.01 MW | F1 | 10.00MW
| 1176 | Positive Reactive Power Level in MVAR | 1 to 65000 | 1 | 0.01 MVAR | F1 | 10.00MVAR
| 1177 | Negative Reactive Power Level in MVAR | 1 to 65000 | 1 | 0.01 MVAR | F1 | 10.00MVAR
POWER FACTOR ALARMS | 1178 | Power Factor Lead 1 Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1179 | Power Factor Lead 1 Pickup Level | 0 to 100 | 1 | 0.01 x PF | F1 | 0.99
| 117A | Power Factor Lead 1 Dropout Level | 0 to 100 | 1 | 0.01 x PF | F1 | 1
| 117B | Power Factor Lead 1 Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 117C | Power Factor Lag 1 Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 117D | Power Factor Lag 1 Pickup Level | 0 to 100 | 1 | 0.01 x PF | F1 | 0.99
| 117E | Power Factor Lag 1 Dropout Level | 0 to 100 | 1 | 0.01 x PF | F1 | 1
| 117F | Power Factor Lag 1 Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1180 | Power Factor Lead 2 Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1181 | Power Factor Lead 2 Pickup Level | 0 to 100 | 1 | 0.01 x PF | F1 | 0.99
| 1182 | Power Factor Lead 2 Dropout Level | 0 to 100 | 1 | 0.01 x PF | F1 | 1
| 1183 | Power Factor Lead 2 Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1184 | Power Factor Lag 2 Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1185 | Power Factor Lag 2 Pickup Level | 0 to 100 | 1 | 0.01 x PF | F1 | 0.99
| 1186 | Power Factor Lag 2 Dropout Level | 0 to 100 | 1 | 0.01 x PF | F1 | 1
| 1187 | Power Factor Lag 2 Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1188 | Reserved
| to |  |  |  |  |  | 
| 118F | Reserved
DEMAND ALARMS | 1190 | Phase A Current Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1191 | Phase A Current Demand Level | 10 to 7500 | 1 | A | F1 | 100 A
| 1192 | Phase B Current Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1193 | Phase B Current Demand Level | 10 to 7500 | 1 | A | F1 | 100 A
| 1194 | Phase C Current Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1195 | Phase C Current Demand Level | 10 to 7500 | 1 | A | F1 | 100 A
| 1196 | Neutral Current Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1197 | Neutral Current Demand Level | 10 to 7500 | 1 | A | F1 | 100 A
| 1198 | Positive Real Power Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1199 | Positive Real Power Demand Level | 1 to 65000 | 1 | kW | F1 | 1000 kW
| 119A | Positive Reactive Power Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 119B | Positive Reactive Power Demand Level | 1 to 65000 | 1 | kvar | F1 | 1000 kvar
| 119C | Apparent Power Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 119D | Apparent Power Demand Level | 1 to 65000 | 1 | kVA | F1 | 1000 kVA
| 119E | Negative Real Power Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 119F | Negative Real Power Demand Level | 1 to 65000 | 1 | kW | F1 | 1000 kW
| 11A0 | Negative Reactive Power Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 11A1 | Negative Reactive Power Demand Level | 1 to 65000 | 1 | kvar | F1 | 1000 kvar
| 11A2 | Reserved
| to |  |  |  |  |  | 
| 11A7 | Reserved
PULSE INPUT ALARMS | 11A8 | Pulse Input 1 Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 11A9 | Pulse Input 1 Level | 1 to 65000 | 1 | --- | F1 | 100
| 11AA | Pulse Input 1 Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 11AB | Reserved
| to |  |  |  |  |  | 
| 11AF | Reserved
MISC. ALARMS | 11B0 | Serial COM1 Failure Alarm Delay | 5 to 61*** | 1 | s | F1 | 61=OFF
| 11B1 | Serial COM2 Failure Alarm Delay | 5 to 61*** | 1 | s | F1 | 61=OFF
| 11B2 | Clock Not Set Alarm | 0 to 1 | 1 | --- | F11 | 1 = ENABLE
| 11B3 | Data Log 1 Percentage Full Alarm Level | 50 to 101*** | 1 | s | F1 | 101=OFF
| 11B4 | Data Log 2 Percentage Full Alarm Level | 50 to 101*** | 1 | s | F1 | 101=OFF
| 11B5 | Reserved
| 11B6 | Reserved
| 11B7 | Reserved
PULSE INPUT ALARMS | 11B8 | Pulse Input 2 Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 11B9 | Pulse Input 2 Level | 1 to 65000 | 1 | --- | F1 | 100
| 11BA | Pulse Input 2 Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 11BB | Pulse Input 3 Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 11BC | Pulse Input 3 Level | 1 to 65000 | 1 | --- | F1 | 100
| 11BD | Pulse Input 3 Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 11BE | Pulse Input 4 Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 11BF | Pulse Input 4 Level | 1 to 65000 | 1 | --- | F1 | 100
| 11C0 | Pulse Input 4 Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 11C1 | Totalized Pulse Input Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 11C2 | Totalized Pulse Input Level | 1 to 65000 | 1 | --- | F1 | 100
| 11C3 | Totalized Pulse Input Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 11C4 | Reserved
| to |  |  |  |  |  | 
| 11C7 | Reserved
SIMULATION | 11C8 | Current/Voltage Simulation | 0 to 1 | 1 | --- | F11 | 0=OFF
| 11C9 | Current/Voltage Simulation Time | 5 to 305 | 5 | min | F1***** | 15 min
| 11CA | Phase A Current | 0 to 10000 | 1 | A | F1 | 0 A
| 11CB | Phase B Current | 0 to 10000 | 1 | A | F1 | 0 A
| 11CC | Phase C Current | 0 to 10000 | 1 | A | F1 | 0 A
| 11CD | Neutral Current | 0 to 10000 | 1 | A | F1 | 0 A
| 11CE | Vax Voltage | 0 to 65000 | 1 | V | F1 | 0 V
| 11CF | Vbx Voltage | 0 to 65000 | 1 | V | F1 | 0 V
| 11D0 | Vcx Voltage | 0 to 65000 | 1 | V | F1 | 0 V
| 11D1 | Phase Angle | 0 to 359 | 1 | degrees | F1 | 0 degrees
| 11D2 | Analog Output Simulation | 0 to 1 | 1 | --- | F11 | 0=OFF
| 11D3 | Analog Output Simulation Time | 5 to 305 | 5 | min | F1***** | 15 min
| 11D4 | Analog Output 1 | 0 to 1201*** | 1 | 0.1 x % | F1 | 1201=OFF
| 11D5 | Analog Output 2 | 0 to 1201*** | 1 | 0.1 x % | F1 | 1201=OFF
| 11D6 | Analog Output 3 | 0 to 1201*** | 1 | 0.1 x % | F1 | 1201=OFF
| 11D7 | Analog Output 4 | 0 to 1201*** | 1 | 0.1 x % | F1 | 1201=OFF
| 11D8 | Analog Input Simulation | 0 to 1 | 1 | --- | F11 | 0=OFF
| 11D9 | Analog Input Simulation Time | 5 to 305 | 5 | min | F1***** | 15 min
| 11DA | Analog Input | 40 to 201 | 1 | 0.1 x mA | F1 | 201=OFF
| 11DB | Switch Input Simulation | 0 to 1 | 1 | --- | F11 | 0=OFF
| 11DC | Switch Input Simulation Time | 5 to 305 | 5 | min | F1***** | 15 min
| 11DD | Switch Input A | 0 to 1 | 1 | --- | F27 | 0=OPEN
| 11DE | Switch Input B | 0 to 1 | 1 | --- | F27 | 0=OPEN
| 11DF | Switch Input C | 0 to 1 | 1 | --- | F27 | 0=OPEN
| 11E0 | Switch Input D | 0 to 1 | 1 | --- | F27 | 0=OPEN
| 11E1 | Reserved
| 11E2 | Reserved
| 11E3 | Reserved
TIME ALARM | 11E4 | Time Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 11E5 | Pickup Time Hours/Minutes | 0 to 65535 | 1 | hr/min | F22 | 12:00
| 11E6 | Pickup Time Seconds | 0 to 59000 | 1000 | ms | F1 | 0
| 11E7 | Dropout Time Hours/Minutes | 0 to 65535 | 1 | hr/min | F22 | 12:00
| 11E8 | Dropout Time Seconds | 0 to 59000 | 1000 | ms | F1 | 0
| 11E9 | Reserved
| to |  |  |  |  |  | 
| 11EF | Reserved
PROGRAM- MABLE MESSAGE | 11F0 | Programmable message chars 1 & 2 | 32 to 127 | 1 | ASCII | F10 | “Ph”
| 11F1 | Programmable message chars 3 & 4 | 32 to 127 | 1 | ASCII | F10 | “on”
| 11F2 | Programmable message chars 5 & 6 | 32 to 127 | 1 | ASCII | F10 | “e:”
| 11F3 | Programmable message chars 7 & 8 | 32 to 127 | 1 | ASCII | F10 | “ 9"
| 11F4 | Programmable message chars 9 & 10 | 32 to 127 | 1 | ASCII | F10 | “05”
| 11F5 | Programmable message chars 11 & 12 | 32 to 127 | 1 | ASCII | F10 | “-2”
| 11F6 | Programmable message chars 13 & 14 | 32 to 127 | 1 | ASCII | F10 | “94”
| 11F7 | Programmable message chars 15 & 16 | 32 to 127 | 1 | ASCII | F10 | “-6”
| 11F8 | Programmable message chars 17 & 18 | 32 to 127 | 1 | ASCII | F10 | “22”
| 11F9 | Programmable message chars 19 & 20 | 32 to 127 | 1 | ASCII | F10 | “2 “
| 11FA | Programmable message chars 21 & 22 | 32 to 127 | 1 | ASCII | F10 | “GE”
| 11FB | Programmable message chars 23 & 24 | 32 to 127 | 1 | ASCII | F10 | “in”
| 11FC | Programmable message chars 25 & 26 | 32 to 127 | 1 | ASCII | F10 | “du”
| 11FD | Programmable message chars 27 & 28 | 32 to 127 | 1 | ASCII | F10 | “st”
| 11FE | Programmable message chars 29 & 30 | 32 to 127 | 1 | ASCII | F10 | “ri”
| 11FF | Programmable message chars 31 & 32 | 32 to 127 | 1 | ASCII | F10 | “al”
| 1200 | Programmable message chars 33 & 34 | 32 to 127 | 1 | ASCII | F10 | “.c”
| 1201 | Programmable message chars 35 & 36 | 32 to 127 | 1 | ASCII | F10 | “om”
| 1202 | Programmable message chars 37 & 38 | 32 to 127 | 1 | ASCII | F10 | “/p”
| 1203 | Programmable message chars 39 & 40 | 32 to 127 | 1 | ASCII | F10 | “m “
| 1204 | Reserved
| to |  |  |  |  |  | 
| 120F | Reserved
FLASH MESSAGE | 1210 | Flash message characters 1 and 2 | 32 to 127 | 1 | ASCII | F10 | “”
| 1211 | Flash message characters 3 and 4 | 32 to 127 | 1 | ASCII | F10 | “”
| 1212 | Flash message characters 5 and 6 | 32 to 127 | 1 | ASCII | F10 | “”
| 1213 | Flash message characters 7 and 8 | 32 to 127 | 1 | ASCII | F10 | “”
| 1214 | Flash message characters 9 and 10 | 32 to 127 | 1 | ASCII | F10 | “”
| 1215 | Flash message characters 11 and 12 | 32 to 127 | 1 | ASCII | F10 | “”
| 1216 | Flash message characters 13 and 14 | 32 to 127 | 1 | ASCII | F10 | “”
| 1217 | Flash message characters 15 and 16 | 32 to 127 | 1 | ASCII | F10 | “”
| 1218 | Flash message characters 17 and 18 | 32 to 127 | 1 | ASCII | F10 | “”
| 1219 | Flash message characters 19 and 20 | 32 to 127 | 1 | ASCII | F10 | “”
| 121A | Flash message characters 21 and 22 | 32 to 127 | 1 | ASCII | F10 | “”
| 121B | Flash message characters 23 and 24 | 32 to 127 | 1 | ASCII | F10 | “”
| 121C | Flash message characters 25 and 26 | 32 to 127 | 1 | ASCII | F10 | “”
FLASH MESSAGE continued | 121D | Flash message characters 27 and 28 | 32 to 127 | 1 | ASCII | F10 | “”
| 121E | Flash message characters 29 and 30 | 32 to 127 | 1 | ASCII | F10 | “”
| 121F | Flash message characters 31 and 32 | 32 to 127 | 1 | ASCII | F10 | “”
| 1220 | Flash message characters 33 and 34 | 32 to 127 | 1 | ASCII | F10 | “”
| 1221 | Flash message characters 35 and 36 | 32 to 127 | 1 | ASCII | F10 | “”
| 1222 | Flash message characters 37 and 38 | 32 to 127 | 1 | ASCII | F10 | “”
| 1223 | Flash message characters 39 and 40 | 32 to 127 | 1 | ASCII | F10 | “”
| 1224 | Reserved
| to |  |  |  |  |  | 
| 125F | Reserved
DATA LOGGER | 1260 1261 | Log 1 Interval (high) Log 1 Interval (low) | 1 to 86400 | 1 | s | F3 | 3600
| 1262 1263 | Log 2 Interval (high) Log 2 Interval (low) | 1 to 86400 | 1 | s | F3 | 3600
| 1264 | Log 1 Mode | 0 to 1 | 1 | --- | F32 | 0 = RUN TO FILL
| 1265 | Log 2 Mode | 0 to 1 | 1 | --- | F32 | 0 = RUN TO FILL
| 1266 | Log Size Determination | 0 to 1 | 1 | --- | F33 | 0 = AUTOMATIC
| 1267 | Log 1 Size | 0 to 100 | 1 | % | F1 | 0%
| 1268 | Data Log Memory Access Block Number | 0 to 511 | 1 | --- | F1 | 0
| 1269 | Stop Data Log 1 | 0 to 1 | 1 | --- | F31 | 0=NO
| 126A | Stop Data Log 2 | 0 to 1 | 1 | --- | F31 | 0=NO
| 126B | Reserved
| to |  |  |  |  |  | 
| 126F | Reserved
| 1270 | Ia Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1271 | Ib Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1272 | Ic Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1273 | Iavg Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1274 | In Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1275 | I Unbalance Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1276 | Van Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1277 | Vbn Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1278 | Vcn Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1279 | Vpavg Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 127A | Vab Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 127B | Vbc Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 127C | Vca Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 127D | Vlavg Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 127E | V Unbalance Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 127F | Pa Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1280 | Qa Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1281 | Sa Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1282 | PFa Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1283 | Pb Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1284 | Qb Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1285 | Sb Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1286 | PFb Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1287 | Pc Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1288 | Qc Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1289 | Sc Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 128A | PFc Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 128B | P3 Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 128C | Q3 Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 128D | S3 Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 128E | PF3 Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 128F | Frequency Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1290 | Positive kWh Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1291 | Negative kWh Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1292 | Positive kvarh Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1293 | Negative kvarh Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1294 | kVAh Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1295 | Ia Demand Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1296 | Ib Demand Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1297 | Ic Demand Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1298 | In Demand Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1299 | P3 Demand Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 129A | Q3 Demand Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 129B | S3 Demand Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 129C | Ia THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 129D | Ib THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 129E | Ic THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 129F | In THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 12A0 | Van THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 12A1 | Vbn THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 12A2 | Vcn THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 12A3 | Vab THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 12A4 | Vbc THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 12A5 | Analog Input Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 12A6 | Reserved
| to |  |  |  |  |  | 
| 12BF | Reserved
EVENT RECORDER | 12C0 | Event Recorder Memory Access Event Number | 0 to 65535 | 1 | --- | F1 | 0
| 12C1 | Event Recorder Operation | 0 to 1 | 1 | --- | F11 | 0 = DISABLE
| 12C2 | Event Recorder Event Enable Flags 1 | 0 to 65535 | 1 | --- | F105 | 65535
| 12C3 | Event Recorder Event Enable Flags 2 | 0 to 65535 | 1 | --- | F106 | 65535
| 12C4 | Event Recorder Event Enable Flags 3 | 0 to 65535 | 1 | --- | F107 | 65535
| 12C5 | Event Recorder Event Enable Flags 4 | 0 to 65535 | 1 | --- | F112 | 65535
| 12C6 | Reserved
| to |  |  |  |  |  | 
| 12CF | Reserved
TRACE MEMORY | 12D0 | Trace Memory Usage | 0 to 2 | 1 | --- | F37 | 0=1x36 cycles
| 12D1 | Trace Memory Trigger Mode | 0 to 1 | 1 | --- | F38 | 0=ONE SHOT
| 12D2 | Ia Overcurrent Trigger Level | 1 to 151*** | 1 | % CT | F1 | 151=OFF
| 12D3 | Ib Overcurrent Trigger Level | 1 to 151*** | 1 | % CT | F1 | 151=OFF
| 12D4 | Ic Overcurrent Trigger Level | 1 to 151*** | 1 | % CT | F1 | 151=OFF
| 12D5 | In Overcurrent Trigger Level | 1 to 151*** |  | % CT | F1 | 151=OFF
| 12D6 | Va Overvoltage Trigger Level | 20 to 151*** | 1 | % VT | F1 | 151=OFF
| 12D7 | Vb Overvoltage Trigger Level | 20 to 151*** | 1 | % VT | F1 | 151=OFF
| 12D8 | Vc Overvoltage Trigger Level | 20 to 151*** | 1 | % VT | F1 | 151=OFF
| 12D9 | Va Undervoltage Trigger Level | 20 to 151*** | 1 | % VT | F1 | 151=OFF
| 12DA | Vb Undervoltage Trigger Level | 20 to 151*** | 1 | % VT | F1 | 151=OFF
| 12DB | Vc Undervoltage Trigger Level | 20 to 151*** | 1 | % VT | F1 | 151=OFF
| 12DC | Switch Input A Trigger | 0 to 2 | 1 | --- | F39 | 0=OFF
| 12DD | Switch Input B Trigger | 0 to 2 | 1 | --- | F39 | 0=OFF
| 12DE | Switch Input C Trigger | 0 to 2 | 1 | --- | F39 | 0=OFF
| 12DF | Switch Input D Trigger | 0 to 2 | 1 | --- | F39 | 0=OFF
| 12E0 | Trace Memory Trigger Delay | 0 to 30 | 1 | cycles | F1 | 0 cycles
| 12E1 | Trace Memory Waveform Selection | 0 to 6 | 1 | --- | F40 | 0=Ia
| 12E2 | Trace Memory Trigger Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 12E3 | Reserved
| to |  |  |  |  |  | 
| 12EF | Reserved
PRODUCT OPTIONS | 12F0 | Product Options Upgrade | 0 to 23 | 1 | --- | F116 | 0
| 12F1 | Product Modifications Upgrade MOD1 | 0 to 999 | 1 | --- | F1 | 0
| 12F2 | Product Modifications Upgrade MOD2 | 0 to 999 | 1 | --- | F1 | 0
| 12F3 | Product Modifications Upgrade MOD3 | 0 to 999 | 1 | --- | F1 | 0
| 12F4 | Product Modifications Upgrade MOD4 | 0 to 999 | 1 | --- | F1 | 0
| 12F5 | Product Modifications Upgrade MOD5 | 0 to 999 | 1 | --- | F1 | 0
| 12F6 | Passcode Input 1 | 32 to 127 | 1 | --- | F10 | 32
| 12F7 | Passcode Input 2 | 32 to 127 | 1 | --- | F10 | 32
| 12F8 | Passcode Input 3 | 32 to 127 | 1 | --- | F10 | 32
| 12F9 | Passcode Input 4 | 32 to 127 | 1 | --- | F10 | 32
| 12FA | Passcode Input 5 | 32 to 127 | 1 | --- | F10 | 32
| 12FB | Passcode Input 6 | 32 to 127 | 1 | --- | F10 | 32
| 12FC | Passcode Input 7 | 32 to 127 | 1 | --- | F10 | 32
| 12FD | Passcode Input 8 | 32 to 127 | 1 | --- | F10 | 32
| 12FE | Passcode Input 9 | 32 to 127 | 1 | --- | F10 | 32
| 12FF | Passcode Input 10 | 32 to 127 | 1 | --- | F10 | 32
| 1300 | Reserved
| to |  |  |  |  |  | 
| 131F | Reserved
Notes:* Data type depends on the Command Operation Code.** Any valid Actual Values or Setpoints address. *** Maximum Setpoint value represents “OFF”.**** Minimum Setpoint value represents “OFF”. ***** Maximum Setpoint value represents “UNLIMITED”.****** Applicable to older revisions with VFD display only

## PQM Data Formats
CODE | DESCRIPTION | BITMASK
* Refer to manual section A.7 - Reading Long Integers From Memory Map - for more information.
F1 | UNSIGNED INTEGER - NUMERICAL DATA | FFFF
F2 | SIGNED INTEGER - NUMERICAL DATA | FFFF
F3* | UNSIGNED LONG INTEGER - NUMERICAL DATA | FFFFFFFF
F4* | SIGNED LONG INTEGER - NUMERICAL DATA | FFFFFFFF
F5 | HARDWARE VERSION CODE | FFFF
| 1 = A | ---
| 2 = B | ---
|  | Ø
| 26 = Z | ---
F6 | UNSIGNED INTEGER - CURRENT KEY PRESS | FFFF
| 0000 = no key | ---
| FE01 = STORE | ---
| FE02 = SETPOINT | ---
| FE04 = MESSAGE RIGHT | ---
| FE08 = VALUE UP | ---
| FD01 = RESET | ---
| FD02 = MESSAGE LEFT | ---
| FD04 = MESSAGE UP | ---
| FD08 = VALUE DOWN | ---
| FB01 = ACTUAL | ---
| FB02 = MESSAGE DOWN | ---
F7 | UNSIGNED INTEGER - COMMAND | FFFF
| 1 = Reset | ---
| 2 = Alarm Relay On | ---
| 3 = Alarm Relay Off | ---
| 4 = Auxiliary Relay 1 On | ---
| 5 = Auxiliary Relay 1 Off | ---
| 6 = Auxiliary Relay 2 On | ---
| 7 = Auxiliary Relay 2 Off | ---
| 8 = Auxiliary Relay 3 On | ---
| 9 = Auxiliary Relay 3 Off | ---
| 10 = Set Clock Time | ---
| 11 = Set Clock Date | ---
| 12 = Display 40 character Flash Message for 5 s | ---
| 13 = Simulate Keypress | ---
| 14 = Clear Energy Values | ---
| 15 = Clear Max. Demand Values | ---
| 16 = Clear Min./Max. Current Values | ---
| 17 = Clear Min./Max. Voltage Values | ---
| 18 = Clear Min./Max. Power Values | ---
| 19 = Clear Max. THD Values | ---
| 20 = Clear Switch Input Pulse Count | ---
| 21 = High Speed Sampling Trigger | ---
| 22 = Upload Mode Entry 2 | ---
| 23 = Upload Mode Entry 1 | ---
F7 con’t | 24 = Factory Setpoints Reload 2 | ---
| 25 = Factory Setpoints Reload 1 | ---
| 26 = Test Relays and LEDs | ---
| 27 = Waveform Capture Trigger | ---
| 28 = Start Data Log(s) | ---
| 29 = Stop Data Log(s) | ---
| 30 = Resize Data Logs (valid only if both logs are stopped) | ---
| 31 = Clear Event Record | ---
| 32= Trigger Trace Memory | ---
| 33= Re-arm Trace Memory | ---
| 34= Clear All Demand | ---
| 35= Clear Min./Max. Frequency | ---
F8 | UNSIGNED INTEGER - KEYPRESS SIMULATION | FFFF
| 49 = '1' = SETPOINT | ---
| 50 = '2' = ACTUAL | ---
| 51 = '3' = RESET | ---
| 52 = '4' = STORE | ---
| 53 = '5' = MESSAGE UP | ---
| 54 = '6' = MESSAGE DOWN | ---
| 55 = '7' = MESSAGE LEFT | ---
| 56 = '8' = MESSAGE RIGHT | ---
| 57 = '9' = VALUE UP | ---
| 97 = 'a' = VALUE DOWN | ---
F9 | UNSIGNED INTEGER - RELAY/LED TEST DATA | FFFF
| Alarm Relay | 1
| Auxiliary Relay 1 | 2
| Auxiliary Relay 2 | 4
| Auxiliary Relay 3 | 8
| ‘ALARM’ LED | 10
| ‘PROGRAM’ LED | 20
| ‘SIMULATION’ LED | 40
| ‘SELF TEST’ LED | 80
| ‘ALARM’ Relay LED | 100
| ‘AUX 1’ Relay LED | 200
| ‘AUX 2’ Relay LED | 400
| ‘AUX 3’ Relay LED | 800
F10 | TWO ASCII CHARACTERS | FFFF
| 32-127 = ASCII Character | 7F00
| 32-127 = ASCII Character | 007F
F11 | UNSIGNED INTEGER - ENABLE/DISABLE | FFFF
| 0 = Disable/OFF | ---
| 1 = Enable/ON | ---
F12 | UNSIGNED INTEGER - MODBUS BAUD RATE | FFFF
| 0 = 1200 | ---
| 1 = 2400 | ---
| 2 = 4800 | ---
| 3 = 9600 | ---
| 4 = 19200 | ---
F13 | UNSIGNED INTEGER - PARITY TYPE | FFFF
| 0 = None | ---
| 1 = Even | ---
| 2 = Odd | ---
F14 | UNSIGNED INTEGER - ANALOG OUTPUT TYPE | FFFF
| 0 = Not Used | ---
| 1 = Phase A Current | ---
| 2 = Phase B Current | ---
| 3 = Phase C Current | ---
| 4 = Neutral Current | ---
| 5 = Average Phase Current | ---
| 6 = Current Unbalance | ---
| 7 = Voltage Van | ---
| 8 = Voltage Vbn | ---
| 9 = Voltage Vcn | ---
| 10 = Voltage Vab | ---
| 11 = Voltage Vbc | ---
| 12 = Voltage Vca | ---
| 13 = Average Phase Voltage | ---
| 14 = Average Line Voltage | ---
| 15 = Voltage Unbalance | ---
| 16 = Frequency | ---
| 17 = 3 Phase Power Factor | ---
| 18 = 3 Phase Real Power (kW) | ---
| 19 = 3 Phase Reactive Power (kvar) | ---
| 20 = 3 Phase Apparent Power (kVA) | ---
| 21 = 3 Phase Real Power (MW) | ---
| 22 = 3 Phase Reactive Power (Mvar) | ---
| 23 = 3 Phase Apparent Power (MVA) | ---
| 24 = Phase A Power Factor | ---
| 25 = Phase A Real Power | ---
| 26 = Phase A Reactive Power | ---
| 27 = Phase A Apparent Power | ---
| 28 = Phase B Power Factor | ---
| 29 = Phase B Real Power | ---
| 30 = Phase B Reactive Power | ---
| 31 = Phase B Apparent Power | ---
| 32 = Phase C Power Factor | ---
| 33 = Phase C Real Power | ---
| 34 = Phase C Reactive Power | ---
| 35 = Phase C Apparent Power | ---
F14 con’t | 36 = 3 Phase Positive Real Energy Used | ---
| 37 = 3 Phase Positive Reactive Energy Used | ---
| 38 = 3 Phase Negative Real Energy Used | ---
| 39 = 3 Phase Negative Reactive Energy Used | ---
| 40 = 3 Phase Apparent Energy Used | ---
| 41 = Phase A Current Demand | ---
| 42 = Phase B Current Demand | ---
| 43 = Phase C Current Demand | ---
| 44 = Neutral Current Demand | ---
| 45 = 3 Phase Real Power Demand | ---
| 46 = 3 Phase Reactive Power Demand | ---
| 47 = 3 Phase Apparent Power Demand | ---
| 48 = Three Phase Current THD | ---
| 49 = Three Phase Voltage THD | ---
| 50 = Phase A Current THD | ---
| 51 = Phase B Current THD | ---
| 52 = Phase C Current THD | ---
| 53 = Voltage Van THD | ---
| 54 = Voltage Vbn THD | ---
| 55 = Voltage Vcn THD | ---
| 56 = Voltage Vab THD | ---
| 57 = Voltage Vbc THD | ---
| 58 = Neutral Current THD | ---
| 59 = Serial Control | ---
F15 | UNSIGNED INTEGER - VT WIRING | FFFF
| 0 = Off | ---
| 1 = 4 Wire Wye / 3 VTs | ---
| 2 = 4 Wire Wye Direct | ---
| 3 = 4 Wire Wye / 2 VTs | ---
| 4 = 3 Wire Delta / 2 VTs | ---
| 5 = 3 Wire Direct | ---
| 6 = Single Phase Direct | ---
F16 | UNSIGNED INTEGER NEUTRAL CURRENT SENSING | FFFF
| 0 = Off | ---
| 1 = Separate CT | ---
| 2 = Calculated | ---
F17 | UNSIGNED INTEGER -FAILSAFE/NON-FAILSAFE | FFFF
| 0 =Non-fail-safe | ---
| 1 = Fail-safe | ---
F18 | UNSIGNED INTEGER - UNLATCHED / LATCHED | FFFF
| 0 = Unlatched | ---
| 1 = Latched | ---
F19 | UNSIGNED INTEGER - AUX RELAY FUNCTION | FFFF
| 0 = Off | ---
| 1 = Aux1 Relay | ---
| 2 = Aux2 Relay | ---
| 3 = Aux3 Relay | ---
F20 | UNSIGNED INTEGER - SWITCH FUNCTION | FFFF
| 0 = Not Used | ---
| 1 = Alarm Relay | ---
| 2 = Auxiliary Relay 1 | ---
| 3 = Auxiliary Relay 2 | ---
| 4 = Auxiliary Relay 3 | ---
| 5 = Pulse Input 1 | ---
| 6 = New Demand Period | ---
| 7 = Setpoint Access | ---
| 8 = Select Main/Alt Analog Output | ---
| 9 = Select Main/Alt Analog Input | ---
| 10 = Pulse Input 2 | ---
| 11 = Pulse Input 3 | ---
| 12 = Pulse Input 4 | ---
| 13 = Clear Energy | ---
| 14 = Clear Demand | ---
F22 | TIME HOURS/MINUTES | FFFF
| Hours: 0 = 12 am, 1 = 1 am,..., 23 = 11 pm | FF00
| Minutes: 0-59 in steps of 1 | 00FF
F23 | UNSIGNED INTEGER - TIME SECONDS | FFFF
| Seconds: 0 = 0.000s,...,59999 = 59.999s | ---
F24 | DATE MONTH/DAY | FFFF
| Month: 1=January,..., 12=December | FF00
| Day: 1-31 in steps of 1 | 00FF
F25 | UNSIGNED INTEGER - DATE YEAR | FFFF
| Year: 1995, 1996, 1997,... | ---
F26 | UNSIGNED INTEGER HARMONIC SPECTRUM PARAMETER | FFFF
| 0 = None | ---
| 1 = Phase A Current | ---
| 2 = Phase B Current | ---
| 3 = Phase C Current | ---
| 4 = Neutral Current | ---
| 5 = Voltage Vax | ---
| 6 = Voltage Vbx | ---
| 7 = Voltage Vcx | ---
F27 | UNSIGNED INTEGER - SWITCH ACTIVATION | FFFF
| 0 = Open | ---
| 1 = Closed | ---
F28 | UNSIGNED INTEGER DEMAND CALCULATION TYPE | FFFF
| 0 = Thermal Exponential | ---
| 1 = Block Interval | ---
| 2 = Rolling Interval | ---
F29 | UNSIGNED INTEGER ALARM/CONTROL RELAY SELECTION | FFFF
| 0 = Off | ---
| 1 = Alarm Relay | ---
| 2 = Auxiliary Relay 1 | ---
| 3 = Auxiliary Relay 2 | ---
| 4 = Auxiliary Relay 3 | ---
F30 | UNSIGNED INTEGER PHASES REQ’D FOR OPERATION | FFFF
| 0 = Any One | ---
| 1 = Any Two | ---
| 2 = All Three | ---
F31 | UNSIGNED INTEGER - YES/NO | FFFF
| 0 = No | ---
| 1 = Yes | ---
F32 | UNSIGNED INTEGER - DATA LOG MODE | FFFF
| 0 = Run to Fill | ---
| 1 = Circulate | ---
F33 | UNSIGNED INTEGER DATA LOG SIZE DETERMINATION | FFFF
| 0 = Automatic | ---
| 1 = From Setpoint | ---
F34 | UNSIGNED INTEGER - DATA LOG SELECTION | FFFF
| 0 = None | ---
| 1 = Log 1 | ---
| 2 = Log 2 | ---
| 3 = Log 1 and Log 2 | ---
F35 | UNSIGNED INTEGER - DATA LOG STATUS | FFFF
| 0 = Stopped | ---
| 1 = Running | ---
F36 | UNSIGNED INTEGER - CAUSE OF EVENT | FFFF
| 0 = No Event | ---
| 1 = Clear Event Record | ---
| 2 = Power On | ---
| 3 = Power Off | ---
| 4 = Reset | ---
| 5 = Setpoint Access Enabled | ---
| 6 = Switch A Alarm | ---
| 7 = Switch B Alarm | ---
| 8 = Switch C Alarm | ---
| 9 = Switch D Alarm | ---
| 10 = COM1 Fail Alarm | ---
| 11 = COM2 Fail Alarm | ---
| 12 = Self Test Alarm | ---
| 13 = Clock Not Set Alarm | ---
| 14 = Parameters Not Set Alarm | ---
| 15 = Underfrequency Alarm | ---
| 16 = Overfrequency Alarm | ---
| 17 = Undercurrent Alarm | ---
| 18 = Overcurrent Alarm | ---
| 19 = Neutral Overcurrent Alarm | ---
| 20 = Undervoltage Alarm | ---
| 21 = Overvoltage Alarm | ---
| 22 = Current Unbalance Alarm | ---
| 23 = Voltage Unbalance Alarm | ---
| 24 = Phase Reversal Alarm | ---
| 25 = Power Factor Lead 1 Alarm | ---
| 26 = Power Factor Lead 2 Alarm | ---
| 27 = Power Factor Lag 1 Alarm | ---
| 28 = Power Factor Lag 2 Alarm | ---
| 29 = Positive kW Alarm | ---
| 30 = Negative kW Alarm | ---
| 31 = Positive kvar Alarm | ---
| 32 = Negative kvar Alarm | ---
| 33 = Positive kW Demand Alarm | ---
| 34 = Positive kvar Demand Alarm | ---
| 35 = Negative kW Demand Alarm | ---
| 36 = Negative kvar Demand Alarm | ---
| 37 = kVA Demand Alarm | ---
| 38 = Phase A Current Demand Alarm | ---
| 39 = Phase B Current Demand Alarm | ---
| 40 = Phase C Current Demand Alarm | ---
| 41 = Neutral Current Demand Alarm | ---
| 42 = Pulse Input 1 Alarm | ---
| 43 = Current THD Alarm | ---
| 44 = Voltage THD Alarm | ---
| 45 = Analog Input Main Alarm | ---
| 46 = Analog Input Alternate Alarm | ---
| 47 = Data Log 1 Alarm | ---
| 48 = Data Log 2 Alarm | ---
| 49 = Switch A Alarm Clear | ---
| 50 = Switch B Alarm Clear | ---
| 51 = Switch C Alarm Clear | ---
| 52 = Switch D Alarm Clear | ---
| 53 = COM1 Fail Alarm Clear | ---
| 54 = COM2 Fail Alarm Clear | ---
| 55 = Self Test Alarm Clear | ---
| 56 = Clock Not Set Alarm Clear | ---
| 57 = Parameters Not Set Alarm Clear | ---
| 58 = Underfrequency Alarm Clear | ---
| 59 = Overfrequency Alarm Clear | ---
| 60 = Undercurrent Alarm Clear | ---
| 61 = Overcurrent Alarm Clear | ---
| 62 = Neutral Overcurrent Alarm Clear | ---
| 63 = Undervoltage Alarm Clear | ---
| 64 = Overvoltage Alarm Clear | ---
| 65 = Current Unbalance Alarm Clear | ---
| 66 = Voltage Unbalance Alarm Clear | ---
| 67 = Phase Reversal Alarm Clear | ---
| 68 = Power Factor Lead 1 Alarm Clear | ---
| 69 = Power Factor Lead 2 Alarm Clear | ---
| 70 = Power Factor Lag 1 Alarm Clear | ---
| 71 = Power Factor Lag 2 Alarm Clear | ---
| 72 = Positive kW Alarm Clear | ---
| 73 = Negative kW Alarm Clear | ---
| 74 = Positive kvar Alarm Clear | ---
| 75 = Negative kvar Alarm Clear | ---
| 76 = Positive kW Demand Alarm Clear | ---
| 77 = Positive kvar Demand Alarm Clear | ---
| 78 = Negative kW Demand Alarm Clear | ---
| 79 = Negative kvar Demand Alarm Clear | ---
| 80 = kVA Demand Alarm Clear | ---
| 81 = Phase A Current Demand Alarm Clear | ---
| 82 = Phase B Current Demand Alarm Clear | ---
| 83 = Phase C Current Demand Alarm Clear | ---
| 84 = Neutral Current Demand Alarm Clear | ---
| 85 = Pulse Input 1 Alarm Clear | ---
| 86 = Current THD Alarm Clear | ---
| 87 = Voltage THD Alarm Clear | ---
| 88 = Analog Input Main Alarm Clear | ---
| 89 = Analog Input Alternate Alarm Clear | ---
| 90 = Data Log 1 Alarm Clear | ---
| 91 = Data Log 2 Alarm Clear | ---
| 92 = Pulse Input 2 Alarm | ---
| 93 = Pulse Input 3 Alarm | ---
| 94 = Pulse Input 4 Alarm | ---
| 95 = Pulse Count Total Alarm | ---
| 96 = Pulse Input 2 Alarm Clear | ---
| 97 = Pulse Input 3 Alarm Clear | ---
| 98 = Pulse Input 4 Alarm Clear | ---
| 99 = Pulse Input Total Alarm Clear | ---
| 100 = Time Alarm | ---
| 101 = Time Alarm Clear | ---
| 102 = Trace Memory Trigger | ---
F37 | TRACE MEMORY USAGE | FFFF
| 0 = 1 x 36 cycles | ---
| 1 = 2 x 18 cycles | ---
| 2 = 3 x 12 cycles | ---
F38 | TRACE MEMORY TRIGGER MODE | FFFF
| 0 = ONE SHOT | ---
| 1 = RETRIGGER | ---
F39 | TRACE MEMORY SWITCH INPUT TRIGGER | FFFF
| 0 = OFF | ---
| 1 = OPEN-TO-CLOSED | ---
| 2 = CLOSED-TO-OPEN | ---
F40 | TRACE MEMORY WAVEFORM SELECTION | FFFF
| 0 = Ia | ---
| 1 = Ib | ---
| 2 = Ic | ---
| 3 = In | ---
| 4 = Va | ---
| 5 = Vb | ---
| 6 = Vc | ---
F41 | TRACE MEMORY TRIGGERS | FFFF
| 0 = Trace Memory Not Triggered | ---
| 1 = Ia Overcurrent | ---
| 2 = Ib Overcurrent | ---
| 3 = Ic Overcurrent | ---
| 4 = In Overcurrent | ---
| 5 = Va Overvoltage | ---
| 6 = Vb Overvoltage | ---
| 7 = Vc Overvoltage | ---
| 8 = Va Undervoltage | ---
| 9 = Vb Undervoltage | ---
| 10 = Vc Undervoltage | ---
| 11 = Switch Input A | ---
| 12 = Switch Input B | ---
| 13 = Switch Input C | ---
| 14 = Switch Input D | ---
| 15 = Serial Communication | ---
F43 | PULSE INPUT TOTALIZATION | FFFF
| 0 = 1+2 | ---
| 1 = 1+3 | ---
| 2 = 1+4 | ---
| 3 = 2+3 | ---
| 4 = 2+4 | ---
| 5 = 3+4 | ---
| 6 = 1+2+3 | ---
| 7 = 1+3+4 | ---
| 8 = 2+3+4 | ---
| 9 = 1+2+3+4 | ---
| 10 = 1+2+4 | ---
F44 | PHASE CT WIRING | FFFF
| 0 = Phase A, B and C | ---
| 1 = Phase A and B only | ---
| 2 = Phase A and C only | ---
| 3 = Phase A only | ---
F47 | DNP PORT | FFFF
| 0 = NONE | ---
| 1 = RS232 | ---
| 2 = COM1 | ---
| 3 = COM2 | ---
F100 | PQM OPTIONS | FFFF
| No Options Installed (Chassis Mount) | 0
| PQM (Display Version) | 1
| T20 (4-20mA Transducer) Option | 2
| T1 (0-1mA Transducer) Option | 4
| C (Control) Option | 8
| A (Power Analysis) Option | 10
| Not Used | 20
| Not Used | 40
| Not Used | 80
| Not Used | 100
| Not Used | 200
| Not Used | 400
| Not Used | 800
| Not Used | 1000
| Not Used | 2000
| Not Used | 4000
| Not Used | 8000
F101 | SWITCH INPUT STATUS (0 = OPEN, 1 = CLOSED) | FFFF
| Not Used | 1
| Not Used | 2
| Not Used | 4
| Not Used | 8
| Not Used | 10
| Not Used | 20
| Not Used | 40
| Not Used | 80
| Switch A | 100
| Switch B | 200
| Switch C | 400
| Switch D | 800
| Not Used | 1000
| Not Used | 2000
| Not Used | 4000
| Not Used | 8000
F102 | LED STATUS FLAGS: (0 = INACTIVE, 1 = ACTIVE) | FFFF
| AUX 1 Relay | 1
| AUX 2 Relay | 2
| AUX 3 Relay | 4
| ALARM | 8
| PROGRAM | 10
| SIMULATION | 20
| ALARM Relay | 40
| SELF TEST | 80
| Not Used | 100
| Not Used | 200
| Not Used | 400
| Not Used | 800
| Not Used | 1000
| Not Used | 2000
| Not Used | 4000
| Not Used | 8000
F103 | LED ATTRIBUTE FLAGS (0 = FLASHING, 1 = SOLID; ACTIVE) | FFFF
| AUX 1 Relay | 1
| AUX 2 Relay | 2
| AUX 3 Relay | 4
| ALARM | 8
| PROGRAM | 10
| SIMULATION | 20
| ALARM Relay | 40
| SELF TEST | 80
| Not Used | 100
| Not Used | 200
| Not Used | 400
| Not Used | 800
| Not Used | 1000
| Not Used | 2000
| Not Used | 4000
| Not Used | 8000
F104 | OUTPUT RELAY FLAG (0=DE-ENERGIZED,1=ENERGIZED) | FFFF
| Alarm Relay | 1
| Auxiliary Relay 1 | 2
| Auxiliary Relay 2 | 4
| Auxiliary Relay 3 | 8
| Not Used | 10
| Not Used | 20
| Not Used | 40
| Not Used | 80
| Not Used | 100
| Not Used | 200
F104 con’t | Not Used | 400
| Not Used | 800
| Not Used | 1000
| Not Used | 2000
| Not Used | 4000
| Not Used | 8000
F105 | ALARM STATUS FLAGS 1: | FFFF
| Phase Undercurrent Alarm | 1
| Phase Overcurrent Alarm | 2
| Neutral Overcurrent Alarm | 4
| Undervoltage Alarm | 8
| Overvoltage Alarm | 10
| Current Unbalance Alarm | 20
| Voltage Unbalance Alarm | 40
| Voltage Phase Reversal | 80
| Power Factor Lead Alarm 1 | 100
| Power Factor Lead Alarm 2 | 200
| Power Factor Lag Alarm 1 | 400
| Power Factor Lag Alarm 2 | 800
| Positive Real Power Alarm | 1000
| Negative Real Power Alarm | 2000
| Positive Reactive Power Alarm | 4000
| Negative Reactive Power Alarm | 8000
F106 | ALARM STATUS FLAGS 2: | FFFF
| Underfrequency Alarm | 1
| Overfrequency Alarm | 2
| Positive Real Power Demand alarm | 4
| Positive Reactive Power Demand Alarm | 8
| Apparent Power Demand Alarm | 10
| Phase A Current Demand Alarm | 20
| Phase B Current Demand Alarm | 40
| Phase C Current Demand Alarm | 80
| Neutral Current Demand Alarm | 100
| Switch A Alarm | 200
| Switch B Alarm | 400
| Switch C Alarm | 800
| Switch D Alarm | 1000
| Internal Fault Alarm | 2000
| Serial COM1 Failure Alarm | 4000
| Serial COM2 Failure Alarm | 8000
F107 | ALARM STATUS FLAGS 3: | FFFF
| Clock Not Set Alarm | 1
| Parameters Not Set Alarm | 2
| Pulse Input 1 Alarm | 4
| Current THD Alarm | 8
| Voltage THD Alarm | 10
| Analog Input Main Alarm | 20
F107 con’t | Analog Input Alt Alarm | 40
| Data Log 1 | 80
| Data Log 2 | 100
| Negative Real Power Demand alarm | 200
| Negative Reactive Power Demand Alarm | 400
| Pulse Input 2 Alarm | 800
| Pulse Input 3 Alarm | 1000
| Pulse Input 4 Alarm | 2000
| Totalized Pulse Input Alarm | 4000
| Time Alarm | 8000
F108 | INTERNAL FAULT ERROR CODE | FFFF
| ADC Reference Out of Range | 1
| HC705 Processor Not Responding | 2
| Switch Input Circuit Fault | 4
| HC705 MOR Byte is Not Programmed | 8
| Not Used | 10
| Not Used | 20
| Not Used | 40
| Not Used | 80
| Not Used | 100
| Not Used | 200
| Not Used | 400
| Not Used | 800
| Not Used | 1000
| Not Used | 2000
| Not Used | 4000
| Not Used | 8000
F109 | GENERAL STATUS | FFFF
| Alarm Present | 1
| Clock Not Set | 2
| Clock Drifting | 4
| Data Log 1 Running | 8
| Data Log 2 Running | 10
| Not Used | 20
| Not Used | 40
| Not Used | 80
| Not Used | 100
| Not Used | 200
| Not Used | 400
| Not Used | 800
| Not Used | 1000
| Not Used | 2000
| Not Used | 4000
| Not Used | 8000
F110 | DATA LOGGER NUMBERS | FFFF
| Log 1 | 1
| Log 2 | 2
F110 con’t | Not Used | 4
| Not Used | 8
| Not Used | 10
| Not Used | 20
| Not Used | 40
| Not Used | 80
| Not Used | 100
| Not Used | 200
| Not Used | 400
| Not Used | 800
| Not Used | 1000
| Not Used | 2000
| Not Used | 4000
| Not Used | 8000
F111 | EVENT RECORD SWITCHES AND RELAY STATUS | FFFF
| Alarm Relay | 1
| Auxiliary Relay 1 | 2
| Auxiliary Relay 2 | 4
| Auxiliary Relay 3 | 8
| Not Used | 10
| Not Used | 20
| Not Used | 40
| Not Used | 80
| Switch A | 100
| Switch B | 200
| Switch C | 400
| Switch D | 800
| Not Used | 1000
| Not Used | 2000
| Not Used | 4000
| Not Used | 8000
F112 | EVENT RECORDER EVENT ENABLE FLAGS 4 | FFFF
| Power On | 1
| Power Off | 2
| Alarm / Control Reset | 4
| Setpoint Access Enable | 8
| Not Used | 10
| Not Used | 20
| Not Used | 40
| Not Used | 80
| Not Used | 100
| Not Used | 200
| Not Used | 400
| Not Used | 800
| Not Used | 1000
| Not Used | 2000
| Not Used | 4000
| Not Used | 8000
F113 | TRACE MEMORY TRIGGERED FLAG STATUS | FFFF
| 0=Trace Memory Not Triggered | ---
| 1=Trace Memory Triggered | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
F114 | POWER ALARMS LEVEL BASE UNITS | FFFF
| 0=kW/kVAR | ---
| 1=MW/MVAR | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
F115 | PHASE OVERCURRENT ACTIVATION | FFFF
| 0=Average | ---
| 1=Maximum | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
F115 con’t | Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
F116 F117 | PRODUCT OPTIONS UPGRADE | FFFF
| 0=PQM/ND | ---
| 1=PQM | ---
| 2=PQM/ND-T20 | ---
| 3=PQM-T20 | ---
| 4=PQM/ND-T1 | ---
| 5=PQM-T1 | ---
| 6=PQM/ND-C | ---
| 7=PQM-C | ---
| 8=PQM/ND-T20-C | ---
| 9=PQM-T20-C | ---
| 10=PQM/ND-T1-C | ---
| 11=PQM-T1-C | ---
| 12=PQM/ND-A | ---
| 13=PQM-A | ---
| 14=PQM/ND-T20-A | ---
| 15=PQM-T20-A | ---
| 16=PQM/ND-T1-A | ---
| 17=PQM-T1-A | ---
| 18=PQM/ND-C-A | ---
| 19=PQM-C-A | ---
| 20=PQM/ND-T20-C-A | ---
| 21=PQM-T20-C-A | ---
| 22=PQM/ND-T1-C-A | ---
| 23=PQM-T1-C-A | ---
| Invalid Serial Number Flag | FFFF
| 0=Serial Number Valid | ---
| 1= Serial Number Invalid | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---
| Not Used | ---

## PQMII Modbus Map
GROUP | ADDR (HEX) | DESCRIPTION | RANGE | STEP VALUE | UNITS and SCALE | FORMAT | FACTORY DEFAULT
Notes: *Data type depends on the Command Operation Code. ** Any valid Actual Values or Setpoints address. *** Maximum Setpoint value represents “OFF”. **** Minimum Setpoint value represents “OFF”. ***** Maximum Setpoint value represents “UNLIMITED”.
Product Information (Input Registers) Addresses: 0000 to 007F
PRODUCT ID | 0 | Product Device Code | --- | --- | --- | F1 | 73
| 1 | Hardware Version Code | --- | --- | --- | F5 | current version
| 2 | Main Software Version Code | --- | --- | --- | F1 | current version
| 3 | Modification File Number 1 | --- | --- | --- | F1 | mod. file number 1
| 4 | Boot Software Version Code | --- | --- | --- | F1 | current version
| 5 | Reserved
| 6 | Product options | --- | --- | --- | F100 | from order code
| 7 | Modification File Number 2 | --- | --- | --- | F1 | mod. file number 2
| 8 | Modification File Number 3 | --- | --- | --- | F1 | mod. file number 3
| 9 | Modification File Number 4 | --- | --- | --- | F1 | mod. file number 4
| 000A | Modification File Number 5 | --- | --- | --- | F1 | mod. file number 5
| 000B | CPU Speed | 0 to 1 | 1 | --- | F45 | 16 MHz
| to | 
| 001F | Reserved
| 20 | Serial Number Character 1 and 2 | --- | --- | ASCII | F10 | 1st, 2nd char.
| 21 | Serial Number Character 3 and 4 | --- | --- | ASCII | F10 | 3rd, 4th char.
| 22 | Serial Number Character 5 and 6 | --- | --- | ASCII | F10 | 5th, 6th char
| 23 | Serial Number Character 7 and 8 | --- | --- | ASCII | F10 | 7th, 8th char.
| 24 | Reserved
| to | 
| 002F | Reserved
| 30 | Manufacture Month/Day | --- | --- | --- | F24 | manf. month/day
| 31 | Manufacture Year | --- | --- | --- | F25 | manufacture year
| 32 | Calibration Month/Day | --- | --- | --- | F24 | cal. month/day
| 33 | Calibration Year | --- | --- | --- | F25 | calibration year
| 34 | Reserved
| 35 | Reserved
| to | 
| 007F | Reserved
Commands (Holding Registers) Addresses: 0080 to 00EF
COMMANDS | 80 | Command Function Code | 5 | --- | --- | F1 | 5
| 81 | Command Operation Code | 1 to 35 | 1 | --- | F7 | 0
| 82 | Command Data 1 | 0 to 65535 | 1 | --- | * | 0
| 83 | Command Data 2 | 0 to 65535 | 1 | --- | F31 | 0
| 84 | Command Data 3 | 0 to 65535 | 1 | --- | F8 | 0
| 85 | Command Data 4 | 0 to 65535 | 1 | --- | F8 | 0
| 86 | Command Data 5 | 0 to 65535 | 1 | --- | F8 | 0
| 87 | Command Data 6 | 0 to 65535 | 1 | --- | F8 | 0
| 88 | Command Data 7 | 0 to 65535 | 1 | --- | F8 | 0
| 89 | Command Data 8 | 0 to 65535 | 1 | --- | F8 | 0
| 008A | Command Data 9 | 0 to 65535 | 1 | --- | F8 | 0
| 008B | Command Data 10 | 0 to 65535 | 1 | --- | F8 | 0
COMMANDS continued | 008C | Command Data 11 | 0 to 65535 | 1 | --- | F8 | 0
| 008D | Reserved
| to | 
| 00EF | Reserved
Broadcast Command (Holding Registers) Addresses: 00F0 to 00FF
BROADCAST COMMAND | 00F0 | Time Hours/Minutes | 0 to 65535 | 1 | hr/min | F22 | N/A
| 00F1 | Time Seconds | 0 to 59999 | 1 | ms | F23 | N/A
| 00F2 | Date Month/Day | 0 to 65535 | 1 | --- | F24 | N/A
| 00F3 | Date Year | 0 to 2037 | 1 | --- | F25 | N/A
| 00F4 | Reserved
| to | 
| 00FF | Reserved
User Definable Register (Input Registers) Addresses: 0100 to 017F
USER DEFINABLE REGISTERS | 100 | User Definable Data 0000 | --- | --- | --- | --- | ---
| 101 | User Definable Data 0001 | --- | --- | --- | --- | ---
| 102 | User Definable Data 0002 | --- | --- | --- | --- | ---
| 103 | User Definable Data 0003 | --- | --- | --- | --- | ---
| 104 | User Definable Data 0004 | --- | --- | --- | --- | ---
| 105 | User Definable Data 0005 | --- | --- | --- | --- | ---
| 106 | User Definable Data 0006 | --- | --- | --- | --- | ---
| 107 | User Definable Data 0007 | --- | --- | --- | --- | ---
| 108 | User Definable Data 0008 | --- | --- | --- | --- | ---
| 109 | User Definable Data 0009 | --- | --- | --- | --- | ---
| 010A | User Definable Data 000A | --- | --- | --- | --- | ---
| 010B | User Definable Data 000B | --- | --- | --- | --- | ---
| to |  |  |  |  |  | 
| 177 | User Definable Data 0077 | --- | --- | --- | --- | ---
| 178 | Reserved
| to | 
| 017F | Reserved
User Definable Register Index (Holding Registers) Addresses: 0180 to 01FF
USER DEFINABLE REGISTER INDEX | 180 | Register address for User Data 0000 | ** | 1 | --- | F1 | 0
| 181 | Register address for User Data 0001 | ** | 1 | --- | F1 | 0
| 182 | Register address for User Data 0002 | ** | 1 | --- | F1 | 0
| 183 | Register address for User Data 0003 | ** | 1 | --- | F1 | 0
| 184 | Register address for User Data 0004 | ** | 1 | --- | F1 | 0
| 185 | Register address for User Data 0005 | ** | 1 | --- | F1 | 0
| 186 | Register address for User Data 0006 | ** | 1 | --- | F1 | 0
| 187 | Register address for User Data 0007 | ** | 1 | --- | F1 | 0
| 188 | Register address for User Data 0008 | ** | 1 | --- | F1 | 0
| 189 | Register address for User Data 0009 | ** | 1 | --- | F1 | 0
| 018A | Register address for User Data 000A | ** | 1 | --- | F1 | 0
| 018B | Register address for User Data 000B | ** | 1 | --- | F1 | 0
| 018C | Register address for User Data 000C | ** | 1 | --- | F1 | 0
| 018D | Register address for User Data 000D | ** | 1 | --- | F1 | 0
| to |  |  |  |  |  | 
| 01F7 | Register address for User Data 0077 | ** | 1 | --- | F1 | 0
USER DEFINABLE REGISTER INDEX continued | 01F8 | Reserved
| to | 
| 01FF | Reserved
Actual Values (Input Registers) Addresses: 0200-0E1F
STATUS | 200 | Switch Input Status | --- | --- | --- | F101 | N/A
| 201 | LED Status Flags | --- | --- | --- | F102 | N/A
| 202 | LED Attribute Flags | --- | --- | --- | F103 | N/A
| 203 | Output Relay Status Flags | --- | --- | --- | F104 | N/A
| 204 | Alarm Active Status Flags 1 | --- | --- | --- | F105 | N/A
| 205 | Alarm Pickup Status Flags 1 | --- | --- | --- | F105 | N/A
| 206 | Alarm Active Status Flags 2 | --- | --- | --- | F106 | N/A
| 207 | Alarm Pickup Status Flags 2 | --- | --- | --- | F106 | N/A
| 208 | Alarm Active Status Flags 3 | --- | --- | --- | F107 | N/A
| 209 | Alarm Pickup Status Flags 3 | --- | --- | --- | F107 | N/A
| 020A | Aux. 1 Active Status Flags 1 | --- | --- | --- | F105 | N/A
| 020B | Aux. 1 Pickup Status Flags 1 | --- | --- | --- | F105 | N/A
| 020C | Aux. 1 Active Status Flags 2 | --- | --- | --- | F106 | N/A
| 020D | Aux. 1 Pickup Status Flags 2 | --- | --- | --- | F106 | N/A
| 020E | Aux. 1 Active Status Flags 3 | --- | --- | --- | F107 | N/A
| 020F | Aux. 1 Pickup Status Flags 3 | --- | --- | --- | F107 | N/A
| 210 | Aux. 2 Active Status Flags 1 | --- | --- | --- | F105 | N/A
| 211 | Aux. 2 Pickup Status Flags 1 | --- | --- | --- | F105 | N/A
| 212 | Aux. 2 Active Status Flags 2 | --- | --- | --- | F106 | N/A
| 213 | Aux. 2 Pickup Status Flags 2 | --- | --- | --- | F106 | N/A
| 214 | Aux. 2 Active Status Flags 3 | --- | --- | --- | F107 | N/A
| 215 | Aux. 2 Pickup Status Flags 3 | --- | --- | --- | F107 | N/A
| 216 | Aux. 3 Active Status Flags 1 | --- | --- | --- | F105 | N/A
| 217 | Aux. 3 Pickup Status Flags 1 | --- | --- | --- | F105 | N/A
| 218 | Aux. 3 Active Status Flags 2 | --- | --- | --- | F106 | N/A
| 219 | Aux. 3 Pickup Status Flags 2 | --- | --- | --- | F106 | N/A
| 021A | Aux. 3 Active Status Flags 3 | --- | --- | --- | F107 | N/A
| 021B | Aux. 3 Pickup Status Flags 3 | --- | --- | --- | F107 | N/A
| 021C | General Status | --- | --- | --- | F109 | N/A
| 021D | Encrypted Passcode | --- | --- | --- | F1 | N/A
| 021E | Reserved
| to |  |  |  |  |  | 
| 022F | Reserved
CLOCK | 230 | Time - Hours/Minutes | --- | --- | --- | F22 | N/A
| 231 | Time - Seconds | --- | --- | --- | F23 | N/A
| 232 | Time - Month/Day | --- | --- | --- | F24 | N/A
| 233 | Time Year | --- | --- | --- | F25 | N/A
| 234 | Reserved
| to |  |  |  |  |  | 
| 023F | Reserved
CURRENT | 240 | Phase A Current | --- | --- | A | F1 | N/A
| 241 | Phase B Current | --- | --- | A | F1 | N/A
CURRENT continued | 242 | Phase C Current | --- | --- | A | F1 | N/A
| 243 | Average Current | --- | --- | A | F1 | N/A
| 244 | Neutral Current | --- | --- | A | F1 | N/A
| 245 | Current Unbalance | --- | --- | 0.1 x% | F1 | N/A
| 246 | Phase A Current - Minimum |  |  | A | F1 | N/A
| 247 | Phase B Current - Minimum |  |  | A | F1 | N/A
| 248 | Phase C Current - Minimum |  |  | A | F1 | N/A
| 249 | Neutral Current - Minimum |  |  | A | F1 | N/A
| 024A | Current Unbalance - Minimum |  |  | 0.1 x% | F1 | N/A
| 024B | Phase A Current - Maximum |  |  | A | F1 | N/A
| 024C | Phase B Current - Maximum |  |  | A | F1 | N/A
| 024D | Phase C Current - Maximum |  |  | A | F1 | N/A
| 024E | Neutral Current - Maximum |  |  | A | F1 | N/A
| 024F | Current Unbalance - Maximum |  |  | 0.1 x% | F1 | N/A
| 250 | Time - Hour/Minutes of Phase A Curr. Min | --- | --- | --- | F22 | N/A
| 251 | Time - Seconds of Phase A Current Min | --- | --- | --- | F23 | N/A
| 252 | Date - Month/Day of Phase A Current Min | --- | --- | --- | F24 | N/A
| 253 | Date - Year of Phase A Current Min | --- | --- | --- | F25 | N/A
| 254 | Time - Hour/Minutes of Phase B Curr. Min | --- | --- | --- | F22 | N/A
| 255 | Time - Seconds of Phase B Current Min | --- | --- | --- | F23 | N/A
| 256 | Date - Month/Day of Phase B Current Min | --- | --- | --- | F24 | N/A
| 257 | Date - Year of Phase B Current Min | --- | --- | --- | F25 | N/A
| 258 | Time - Hour/Minutes of Phase C Curr. Min | --- | --- | --- | F22 | N/A
| 259 | Time - Seconds of Phase C Current Min | --- | --- | --- | F23 | N/A
| 025A | Date - Month/Day of Phase C Current Min | --- | --- | --- | F24 | N/A
| 025B | Date - Year of Phase C Current Min | --- | --- | --- | F25 | N/A
| 025C | Time - Hour/Minutes of Neutral Current Min | --- | --- | --- | F22 | N/A
| 025D | Time - Seconds of Neutral Current Min | --- | --- | --- | F23 | N/A
| 025E | Date - Month/Day of Neutral Current Min | --- | --- | --- | F24 | N/A
| 025F | Date - Year of Neutral Current Min | --- | --- | --- | F25 | N/A
| 260 | Time - Hour/Minutes of Current Unbal. Min | --- | --- | --- | F22 | N/A
| 261 | Time - Seconds of Current Unbalance Min | --- | --- | --- | F23 | N/A
| 262 | Date - Month/Day of Current Unbal. Min | --- | --- | --- | F24 | N/A
| 263 | Date - Year of Current Unbalance Min | --- | --- | --- | F25 | N/A
| 264 | Time - Hour/Minutes of Phase A Curr. Max | --- | --- | --- | F22 | N/A
| 265 | Time - Seconds of Phase A Current Max | --- | --- | --- | F23 | N/A
| 266 | Date - Month/Day of Phase A Current Max | --- | --- | --- | F24 | N/A
| 267 | Date - Year of Phase A Current Max | --- | --- | --- | F25 | N/A
| 268 | Time - Hour/Minutes of Phase B Curr. Max | --- | --- | --- | F22 | N/A
CURRENT continued | 269 | Time - Seconds of Phase B Current Max | --- | --- | --- | F23 | N/A
| 026A | Date - Month/Day of Phase B Current Max | --- | --- | --- | F24 | N/A
| 026B | Date - Year of Phase B Current Max | --- | --- | --- | F25 | N/A
| 026C | Time - Hour/Minutes of Phase C Curr. Max | --- | --- | --- | F22 | N/A
| 026D | Time - Seconds of Phase C Current Max | --- | --- | --- | F23 | N/A
| 026E | Date - Month/Day of Phase C Current Max | --- | --- | --- | F24 | N/A
| 026F | Date - Year of Phase C Current Max | --- | --- | --- | F25 | N/A
| 270 | Time - Hour/Minutes of Neutral Current Max | --- | --- | --- | F22 | N/A
| 271 | Time - Seconds of Neutral Current Max | --- | --- | --- | F23 | N/A
| 272 | Date - Month/Day of Neutral Current Max | --- | --- | --- | F24 | N/A
| 273 | Date - Year of Neutral Current Max | --- | --- | --- | F25 | N/A
| 274 | Time - Hour/Minutes of Current Unbal. Max | --- | --- | --- | F22 | N/A
| 275 | Time - Seconds of Current Unbal. Max | --- | --- | --- | F23 | N/A
| 276 | Date - Month/Day of Current Unbal. Max | --- | --- | --- | F24 | N/A
| 277 | Date - Year of Current Unbalance Max | --- | --- | --- | F25 | N/A
| 278 | Reserved
| to |  |  |  |  |  | 
| 027F | Reserved
VOLTAGE | 280 | Voltage Van (High) | --- | --- | V | F3 | N/A
| 281 | Voltage Van (Low)
| 282 | Voltage Vbn (High) | --- | --- | V | F3 | N/A
| 283 | Voltage Vbn (Low)
| 284 | Voltage Vcn (High) | --- | --- | V | F3 | N/A
| 285 | Voltage Vcn (Low)
| 286 | Average Phase Voltage (High) | --- | --- | V | F3 | N/A
| 287 | Average Phase Voltage (Low)
| 288 | Voltage Vab (High) | --- | --- | V | F3 | N/A
| 289 | Voltage Vab (Low)
| 028A | Voltage Vbc (High) | --- | --- | V | F3 | N/A
| 028B | Voltage Vbc (Low)
| 028C | Voltage Vca (High) | --- | --- | V | F3 | N/A
| 028D | Voltage Vca (Low)
| 028E | Average Line Voltage (High) | --- | --- | V | F3 | N/A
| 028F | Average Line Voltage (Low)
| 290 | Voltage Unbalance | --- | --- | 0.1 x % | F1 | N/A
| 291 | Voltage Van - Minimum (high) | --- | --- | V | F3 | N/A
| 292 | Voltage Van - Minimum (Low)
| 293 | Voltage Vbn - Minimum (high) | --- | --- | V | F3 | N/A
| 294 | Voltage Vbn - Minimum (Low)
| 295 | Voltage Vcn - Minimum (high) | --- | --- | V | F3 | N/A
| 296 | Voltage Vcn - Minimum (Low)
| 297 | Voltage Vab - Minimum (high) | --- | --- | V | F3 | N/A
| 298 | Voltage Vab - Minimum (Low)
| 299 | Voltage Vbc - Minimum (high) | --- | --- | V | F3 | N/A
| 029A | Voltage Vbc - Minimum (Low)
| 029B | Voltage Vca - Minimum (high) | --- | --- | V | F3 | N/A
| 029C | Voltage Vca - Minimum (Low)
| 029D | Voltage Unbalance - Minimum | --- | --- | 0.1 x% | F1 | N/A
| 029E | Voltage Van - Maximum (high) | --- | --- | V | F3 | N/A
| 029F | Voltage Van - Maximum (Low)
| 02A0 | Voltage Vbn - Maximum (high) | --- | --- | V | F3 | N/A
| 02A1 | Voltage Vbn - Maximum (Low)
| 02A2 | Voltage Vcn - Maximum (high) | --- | --- | V | F3 | N/A
| 02A3 | Voltage Vcn - Maximum (Low)
| 02A4 | Voltage Vab - Maximum (high) | --- | --- | V | F3 | N/A
| 02A5 | Voltage Vab - Maximum (Low)
| 02A6 | Voltage Vbc - Maximum (high) | --- | --- | V | F3 | N/A
| 02A7 | Voltage Vbc - Maximum (Low)
| 02A8 | Voltage Vca - Maximum (high) | --- | --- | V | F3 | N/A
| 02A9 | Voltage Vca - Maximum (Low)
| 02AA | Voltage Unbalance - Maximum | --- | --- | 0.1 x% | F1 | N/A
| 02AB | Time - Hour/Minutes of Voltage Van Min | --- | --- | --- | F22 | N/A
| 02AC | Time - Seconds of Voltage Van Min | --- | --- | --- | F23 | N/A
| 02AD | Date - Month/Day of Voltage Van Min | --- | --- | --- | F24 | N/A
| 02AE | Date - Year of Voltage Van Min | --- | --- | --- | F25 | N/A
| 02AF | Time - Hour/Minutes of Voltage Vbn Min | --- | --- | --- | F22 | N/A
| 02B0 | Time - Seconds of Voltage Vbn Min | --- | --- | --- | F23 | N/A
| 02B1 | Date - Month/Day of Voltage Vbn Min | --- | --- | --- | F24 | N/A
| 02B2 | Date - Year of Voltage Vbn Min | --- | --- | --- | F25 | N/A
| 02B3 | Time - Hour/Minutes of Voltage Vcn Min | --- | --- | --- | F22 | N/A
| 02B4 | Time - Seconds of Voltage Vcn Min | --- | --- | --- | F23 | N/A
| 02B5 | Date - Month/Day of Voltage Vcn Min | --- | --- | --- | F24 | N/A
| 02B6 | Date - Year of Voltage Vcn Min | --- | --- | --- | F25 | N/A
| 02B7 | Time - Hour/Minutes of Voltage Vab Min | --- | --- | --- | F22 | N/A
| 02B8 | Time - Seconds of Voltage Vab Min | --- | --- | --- | F23 | N/A
| 02B9 | Date - Month/Day of Voltage Vab Min | --- | --- | --- | F24 | N/A
| 02BA | Date - Year of Voltage Vab Min | --- | --- | --- | F25 | N/A
| 02BB | Time - Hour/Minutes of Voltage Vbc Min | --- | --- | --- | F22 | N/A
| 02BC | Time - Seconds of Voltage Vbc Min | --- | --- | --- | F23 | N/A
| 02BD | Date - Month/Day of Voltage Vbc Min | --- | --- | --- | F24 | N/A
| 02BE | Date - Year of Voltage Vbc Min | --- | --- | --- | F25 | N/A
| 02BF | Time - Hour/Minutes of Voltage Vca Min | --- | --- | --- | F22 | N/A
VOLTAGE continued | 02C0 | Time - Seconds of Voltage Vca Min | --- | --- | --- | F23 | N/A
| 02C1 | Date - Month/Day of Voltage Vca Min | --- | --- | --- | F24 | N/A
| 02C2 | Date - Year of Voltage Vca Min | --- | --- | --- | F25 | N/A
| 02C3 | Time - Hour/Minutes of Voltage Unbal. Min | --- | --- | --- | F22 | N/A
| 02C4 | Time - Seconds of Voltage Unbalance Min | --- | --- | --- | F23 | N/A
| 02C5 | Date - Month/Day of Voltage Unbal. Min | --- | --- | --- | F24 | N/A
| 02C6 | Date - Year of Voltage Unbalance Min | --- | --- | --- | F25 | N/A
| 02C7 | Time - Hour/Minutes of Voltage Van Max | --- | --- | --- | F22 | N/A
| 02C8 | Time - Seconds of Voltage Van Max | --- | --- | --- | F23 | N/A
| 02C9 | Date - Month/Day of Voltage Van Max | --- | --- | --- | F24 | N/A
| 02CA | Date - Year of Voltage Van Max | --- | --- | --- | F25 | N/A
| 02CB | Time - Hour/Minutes of Voltage Vbn Max | --- | --- | --- | F22 | N/A
| 02CC | Time - Seconds of Voltage Vbn Max | --- | --- | --- | F23 | N/A
| 02CD | Date - Month/Day of Voltage Vbn Max | --- | --- | --- | F24 | N/A
| 02CE | Date - Year of Voltage Vbn Max | --- | --- | --- | F25 | N/A
| 02CF | Time - Hour/Minutes of Voltage Vcn Max | --- | --- | --- | F22 | N/A
| 02D0 | Time - Seconds of Voltage Vcn Max | --- | --- | --- | F23 | N/A
| 02D1 | Date - Month/Day of Voltage Vcn Max | --- | --- | --- | F24 | N/A
| 02D2 | Date - Year of Voltage Vcn Max | --- | --- | --- | F25 | N/A
| 02D3 | Time - Hour/Minutes of Voltage Vab Max | --- | --- | --- | F22 | N/A
| 02D4 | Time - Seconds of Voltage Vab Max | --- | --- | --- | F23 | N/A
| 02D5 | Date - Month/Day of Voltage Vab Max | --- | --- | --- | F24 | N/A
| 02D6 | Date - Year of Voltage Vab Max | --- | --- | --- | F25 | N/A
| 02D7 | Time - Hour/Minutes of Voltage Vbc Max | --- | --- | --- | F22 | N/A
| 02D8 | Time - Seconds of Voltage Vbc Max | --- | --- | --- | F23 | N/A
| 02D9 | Date - Month/Day of Voltage Vbc Max | --- | --- | --- | F24 | N/A
| 02DA | Date - Year of Voltage Vbc Max | --- | --- | --- | F25 | N/A
| 02DB | Time - Hour/Minutes of Voltage Vca Max | --- | --- | --- | F22 | N/A
| 02DC | Time - Seconds of Voltage Vca Max | --- | --- | --- | F23 | N/A
| 02DD | Date - Month/Day of Voltage Vca Max | --- | --- | --- | F24 | N/A
| 02DE | Date - Year of Voltage Vca Max | --- | --- | --- | F25 | N/A
| 02DF | Time - Hour/Minutes of Voltage Unbal. Max | --- | --- | --- | F22 | N/A
| 2 | Time - Seconds of Voltage Unbalance Max | --- | --- | --- | F23 | N/A
| 20 | Date - Month/Day of Voltage Unbalance Max | --- | --- | --- | F24 | N/A
| 200 | Date - Year of Voltage Unbalance Max | --- | --- | --- | F25 | N/A
| 2000 | Reserved
| 20000 | Reserved
| 200000 | Reserved
| 02D6 | Reserved
| 20000000 | Va Phasor Angle | --- | --- | ° lag | F1
VOLTAGE continued | 200000000 | Vb Phasor Angle | --- | --- | ° lag | F1
| 2000000000 | Vc Phasor Angle | --- | --- | ° lag | F1
| 02EA | Ia Phasor Angle | --- | --- | ° lag | F1
| 02EB | Ib Phasor Angle | --- | --- | ° lag | F1
| 02EC | Ic Phasor Angle | --- | --- | ° lag | F1
| 02ED | Reserved
| 02EE | Reserved
| 02EF | Reserved
POWER | 02F0 | 3 Phase Real Power (high) | --- | --- | 0.01 x kW | F4 | N/A
| 02F1 | 3 Phase Real Power (low)
| 02F2 | 3 Phase Reactive Power (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 02F3 | 3 Phase Reactive Power (low)
| 02F4 | 3 Phase Apparent Power (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 02F5 | 3 Phase Apparent Power (low)
| 02F6 | 3 Phase Power Factor | --- | --- | 0.01 x PF | F2 | N/A
| 02F7 | Phase A Real Power (high) | --- | --- | 0.01 x kW | F4 | N/A
| 02F8 | Phase A Real Power (low)
| 02F9 | Phase A Reactive Power (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 02FA | Phase A Reactive Power (low)
| 02FB | Phase A Apparent Power (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 02FC | Phase A Apparent Power (low)
| 02FD | Phase A Power Factor | --- | --- | 0.01 x PF | F2 | N/A
| 02FE | Phase B Real Power (high) | --- | --- | 0.01 x kW | F4 | N/A
| 02FF | Phase B Real Power (low)
| 300 | Phase B Reactive Power (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 301 | Phase B Reactive Power (low)
| 302 | Phase B Apparent Power (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 303 | Phase B Apparent Power (low)
| 304 | Phase B Power Factor | --- | --- | 0.01 x PF | F2 | N/A
| 305 | Phase C Real Power (high) | --- | --- | 0.01 x kW | F4 | N/A
| 306 | Phase C Real Power (low)
| 307 | Phase C Reactive Power (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 308 | Phase C Reactive Power (low)
| 309 | Phase C Apparent Power (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 030A | Phase C Apparent Power (low)
| 030B | Phase C Power Factor | --- | --- | 0.01 x PF | F2 | N/A
| 030C | 3 Phase Real Power - Minimum (high) | --- | --- | 0.01 x kW | F4 | N/A
| 030D | 3 Phase Real Power - Minimum (low)
| 030E | 3 Phase Reactive Power - Minimum (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 030F | 3 Phase Reactive Power - Minimum (low)
| 310 | 3 Phase Apparent Power - Minimum (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 311 | 3 Phase Apparent Power - Minimum (low)
| 312 | 3 Phase Power Factor - Minimum | --- | --- | 0.01 x PF | F2 | N/A
POWER continued | 313 | 3 Phase Real Power - Maximum (high) | --- | --- | 0.01 x kW | F4 | N/A
| 314 | 3 Phase Real Power - Maximum (low)
| 315 | 3 Phase Reactive Power - Maximum (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 316 | 3 Phase Reactive Power - Maximum (low)
| 317 | 3 Phase Apparent Power - Maximum (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 318 | 3 Phase Apparent Power - Maximum (low)
| 319 | 3 Phase Power Factor - Maximum | --- | --- | 0.01 x PF | F2 | N/A
| 031A | Phase A Real Power - Minimum (high) | --- | --- | 0.01 x kW | F4 | N/A
| 031B | Phase A Real Power - Minimum (low)
| 031C | Phase A Reactive Power - Minimum (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 031D | Phase A Reactive Power - Minimum (low)
| 031E | Phase A Apparent Power - Minimum (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 031F | Phase A Apparent Power - Minimum (low)
| 320 | Phase A Power Factor - Minimum | --- | --- | 0.01 xPF | F2 | N/A
| 321 | Phase A Real Power - Maximum (high) | --- | --- | 0.01 x kW | F4 | N/A
| 322 | Phase A Real Power - Maximum (low)
| 323 | Phase A Reactive Power - Maximum (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 324 | Phase A Reactive Power - Maximum (low)
| 325 | Phase A Apparent Power - Maximum (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 326 | Phase A Apparent Power - Maximum (low)
| 327 | Phase A Power Factor - Maximum | --- | --- | 0.01 x PF | F2 | N/A
| 328 | Phase B Real Power - Minimum (high) | --- | --- | 0.01 x kW | F4 | N/A
| 329 | Phase B Real Power - Minimum (low)
| 032A | Phase B Reactive Power - Minimum (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 032B | Phase B Reactive Power - Minimum (low)
| 032C | Phase B Apparent Power - Minimum (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 032D | Phase B Apparent Power - Minimum (low)
| 032E | Phase B Power Factor - Minimum | --- | --- | 0.01 x PF | F2 | N/A
| 032F | Phase B Real Power - Maximum (high) | --- | --- | 0.01 x kW | F4 | N/A
| 330 | Phase B Real Power - Maximum (low)
| 331 | Phase B Reactive Power - Maximum (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 332 | Phase B Reactive Power - Maximum (low)
| 333 | Phase B Apparent Power - Maximum (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 334 | Phase B Apparent Power - Maximum (low)
| 335 | Phase B Power Factor - Maximum | --- | --- | 0.01 x PF | F2 | N/A
POWER continued | 336 | Phase C Real Power - Minimum (high) | --- | --- | 0.01 x kW | F4 | N/A
| 337 | Phase C Real Power - Minimum (low)
| 338 | Phase C Reactive Power - Minimum (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 339 | Phase C Reactive Power - Minimum (low)
| 033A | Phase C Apparent Power - Minimum (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 033B | Phase C Apparent Power - Minimum (low)
| 033C | Phase C Power Factor - Minimum | --- | --- | 0.01 x PF | F2 | N/A
| 033D | Phase C Real Power - Maximum (high) | --- | --- | 0.01 x kW | F4 | N/A
| 033E | Phase C Real Power - Maximum (low)
| 033F | Phase C Reactive Power - Maximum (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 340 | Phase C Reactive Power - Maximum (low)
| 341 | Phase C Apparent Power - Maximum (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 342 | Phase C Apparent Power - Maximum (low)
| 343 | Phase C Power Factor - Maximum | --- | --- | 0.01 x PF | F2 | N/A
| 344 | Time - Hour/Minutes of Real Power Min | --- | --- | --- | F22 | N/A
| 345 | Time - Seconds of Real Power Min | --- | --- | --- | F23 | N/A
| 346 | Date - Month/Day of Real Power Min | --- | --- | --- | F24 | N/A
| 347 | Date - Year of Real Power Min | --- | --- | --- | F25 | N/A
| 348 | Time - Hour/Minutes of Reactive Pwr Min | --- | --- | --- | F22 | N/A
| 349 | Time - Seconds of Reactive Power Min | --- | --- | --- | F23 | N/A
| 034A | Date - Month/Day of Reactive Power Min | --- | --- | --- | F24 | N/A
| 034B | Date - Year of Reactive Power Min | --- | --- | --- | F25 | N/A
| 034C | Time - Hour/Minutes of Apparent Pwr Min | --- | --- | --- | F22 | N/A
| 034D | Time - Seconds of Apparent Power Min | --- | --- | --- | F23 | N/A
| 034E | Date - Month/Day of Apparent Power Min | --- | --- | --- | F24 | N/A
| 034F | Date - Year of Apparent Power Min | --- | --- | --- | F25 | N/A
| 350 | Time - Hour/Minutes of Power Factor Min | --- | --- | --- | F22 | N/A
| 351 | Time - Seconds of Power Factor Min | --- | --- | --- | F23 | N/A
| 352 | Date - Month/Day of Power Factor Min | --- | --- | --- | F24 | N/A
| 353 | Date - Year of Power Factor Min | --- | --- | --- | F25 | N/A
| 354 | Time - Hour/Minutes of Real Power Max | --- | --- | --- | F22 | N/A
| 355 | Time - Seconds of Real Power Max | --- | --- | --- | F23 | N/A
| 356 | Date - Month/Day of Real Power Max | --- | --- | --- | F24 | N/A
| 357 | Date - Year of Real Power Max | --- | --- | --- | F25 | N/A
| 358 | Time - Hour/Minutes of Reactive Pwr Max | --- | --- | --- | F22 | N/A
POWER continued | 359 | Time - Seconds of Reactive Power Max | --- | --- | --- | F23 | N/A
| 035A | Date - Month/Day of Reactive Pwr Max | --- | --- | --- | F24 | N/A
| 035B | Date - Year of Reactive Power Max | --- | --- | --- | F25 | N/A
| 035C | Time - Hour/Minutes of Apparent Pwr Max | --- | --- | --- | F22 | N/A
| 035D | Time - Seconds of Apparent Pwr Max | --- | --- | --- | F23 | N/A
| 035E | Date - Month/Day of Apparent Pwr Max | --- | --- | --- | F24 | N/A
| 035F | Date - Year of Apparent Power Max | --- | --- | --- | F25 | N/A
| 360 | Time - Hour/Minutes of Power Factor Max | --- | --- | --- | F22 | N/A
| 361 | Time - Seconds of Power Factor Max | --- | --- | --- | F23 | N/A
| 362 | Date - Month/Day of Power Factor Max | --- | --- | --- | F24 | N/A
| 363 | Date - Year of Power Factor Max | --- | --- | --- | F25 | N/A
| 364 | Time - Hour/Min of Phase A Real Pwr Min | --- | --- | --- | F22 | N/A
| 365 | Time - Seconds of Phase A Real Pwr Min | --- | --- | --- | F23 | N/A
| 366 | Date - Month/Day of Phase A Real Pwr Min | --- | --- | --- | F24 | N/A
| 367 | Date - Year of Phase A Real Pwr Min | --- | --- | --- | F25 | N/A
| 368 | Time - Hour/Min of Phase A React Pwr Min | --- | --- | --- | F22 | N/A
| 369 | Time - Seconds of Phase A React Pwr Min | --- | --- | --- | F23 | N/A
| 036A | Date - Month/Day of Phase A React Pwr Min | --- | --- | --- | F24 | N/A
| 036B | Date - Year of Phase A Reactive Pwr Min | --- | --- | --- | F25 | N/A
| 036C | Time - Hour/Min of Phase A App Pwr Min | --- | --- | --- | F22 | N/A
| 036D | Time - Seconds of Phase A App Pwr Min | --- | --- | --- | F23 | N/A
| 036E | Date - Month/Day of Phase A App Pwr Min | --- | --- | --- | F24 | N/A
| 036F | Date - Year of Phase A Apparent Pwr Min | --- | --- | --- | F25 | N/A
| 370 | Time - Hour/Minutes of Phase A PF Min | --- | --- | --- | F22 | N/A
| 371 | Time - Seconds of Phase A PF Min | --- | --- | --- | F23 | N/A
| 372 | Date - Month/Day of Phase A PF Min | --- | --- | --- | F24 | N/A
| 373 | Date - Year of Phase A Power Factor Min | --- | --- | --- | F25 | N/A
| 374 | Time - Hour/Min of Phase A Real Pwr Max | --- | --- | --- | F22 | N/A
| 375 | Time - Seconds of Phase A Real Pwr Max | --- | --- | --- | F23 | N/A
| 376 | Date - Month/Day of Phase A Real Pwr Max | --- | --- | --- | F24 | N/A
| 377 | Date - Year of Phase A Real Power Max | --- | --- | --- | F25 | N/A
| 378 | Time - Hour/Min of Phase A React Pwr Max | --- | --- | --- | F22 | N/A
| 379 | Time - Seconds of Phase A React Pwr Max | --- | --- | --- | F23 | N/A
| 037A | Date - Mnth/Day of Phase A React Pwr Max | --- | --- | --- | F24 | N/A
POWER continued | 037B | Date - Year of Phase A Reactive Pwr Max | --- | --- | --- | F25 | N/A
| 037C | Time - Hour/Min of Phase A App Pwr Max | --- | --- | --- | F22 | N/A
| 037D | Time - Seconds of Phase A App Pwr Max | --- | --- | --- | F23 | N/A
| 037E | Date - Month/Day of Phase A App Pwr Max | --- | --- | --- | F24 | N/A
| 037F | Date - Year of Phase A Apparent Pwr Max | --- | --- | --- | F25 | N/A
| 380 | Time - Hour/Minutes of Phase A PF Max | --- | --- | --- | F22 | N/A
| 381 | Time - Seconds of Phase A PF Max | --- | --- | --- | F23 | N/A
| 382 | Date - Month/Day of Phase A PF Max | --- | --- | --- | F24 | N/A
| 383 | Date - Year of Phase A Power Factor Max | --- | --- | --- | F25 | N/A
| 384 | Time - Hour/Min of Phase B Real Pwr Min | --- | --- | --- | F22 | N/A
| 385 | Time - Seconds of Phase B Real Pwr Min | --- | --- | --- | F23 | N/A
| 386 | Date - Month/Day of Phase B Real Pwr Min | --- | --- | --- | F24 | N/A
| 387 | Date - Year of Phase B Real Power Min | --- | --- | --- | F25 | N/A
| 388 | Time - Hour/Min of Phase B React Pwr Min | --- | --- | --- | F22 | N/A
| 389 | Time - Seconds of Phase B React Pwr Min | --- | --- | --- | F23 | N/A
| 038A | Date - Month/Day of Phase B React Pwr Min | --- | --- | --- | F24 | N/A
| 038B | Date - Year of Phase B Reactive Pwr Min | --- | --- | --- | F25 | N/A
| 038C | Time - Hour/Min of Phase B App Pwr Min | --- | --- | --- | F22 | N/A
| 038D | Time - Seconds of Phase B App Pwr Min | --- | --- | --- | F23 | N/A
| 038E | Date - Month/Day of Phase B App Pwr Min | --- | --- | --- | F24 | N/A
| 038F | Date - Year of Phase B Apparent Pwr Min | --- | --- | --- | F25 | N/A
| 390 | Time - Hour/Minutes of Phase B PF Min | --- | --- | --- | F22 | N/A
| 391 | Time - Seconds of Phase B PF Min | --- | --- | --- | F23 | N/A
| 392 | Date - Month/Day of Phase B PF Min | --- | --- | --- | F24 | N/A
| 393 | Date - Year of Phase B PF Min | --- | --- | --- | F25 | N/A
| 394 | Time - Hour/Min of Phase B Real Pwr Max | --- | --- | --- | F22 | N/A
| 395 | Time - Seconds of Phase B Real Pwr Max | --- | --- | --- | F23 | N/A
| 396 | Date - Month/Day of Phase B Real Pwr Max | --- | --- | --- | F24 | N/A
| 397 | Date - Year of Phase B Real Power Max | --- | --- | --- | F25 | N/A
| 398 | Time - Hour/Min of Phase B React Pwr Max | --- | --- | --- | F22 | N/A
| 399 | Time - Seconds of Phase B React Pwr Max | --- | --- | --- | F23 | N/A
| 039A | Date - Mnth/Day of Phase B React Pwr Max | --- | --- | --- | F24 | N/A
| 039B | Date - Year of Phase B Reactive Pwr Max | --- | --- | --- | F25 | N/A
POWER continued | 039C | Time - Hour/Min of Phase B App Pwr Max | --- | --- | --- | F22 | N/A
| 039D | Time - Seconds of Phase B App Pwr Max | --- | --- | --- | F23 | N/A
| 039E | Date - Month/Day of Phase B App Pwr Max | --- | --- | --- | F24 | N/A
| 039F | Date - Year of Phase B Apparent Pwr Max | --- | --- | --- | F25 | N/A
| 03A0 | Time - Hour/Minutes of Phase B PF Max | --- | --- | --- | F22 | N/A
| 03A1 | Time - Seconds of Phase B PF Max | --- | --- | --- | F23 | N/A
| 03A2 | Date - Month/Day of Phase B PF Max | --- | --- | --- | F24 | N/A
| 03A3 | Date - Year of Phase B Power Factor Max | --- | --- | --- | F25 | N/A
| 03A4 | Time - Hour/Min of Phase C Real Pwr Min | --- | --- | --- | F22 | N/A
| 03A5 | Time - Seconds of Phase C Real Pwr Min | --- | --- | --- | F23 | N/A
| 03A6 | Date - Month/Day of Phase C Real Pwr Min | --- | --- | --- | F24 | N/A
| 03A7 | Date - Year of Phase C Real Power Min | --- | --- | --- | F25 | N/A
| 03A8 | Time - Hour/Min of Phase C React Pwr Min | --- | --- | --- | F22 | N/A
| 03A9 | Time - Seconds of Phase C React Pwr Min | --- | --- | --- | F23 | N/A
| 03AA | Date - Mnth/Day of Phase C React Pwr Min | --- | --- | --- | F24 | N/A
| 03AB | Date - Year of Phase C Reactive Pwr Min | --- | --- | --- | F25 | N/A
| 03AC | Time - Hour/Min of Phase C App Pwr Min | --- | --- | --- | F22 | N/A
| 03AD | Time - Seconds of Phase C App Pwr Min | --- | --- | --- | F23 | N/A
| 03AE | Date - Month/Day of Phase C App Pwr Min | --- | --- | --- | F24 | N/A
| 03AF | Date - Year of Phase C Apparent Pwr Min | --- | --- | --- | F25 | N/A
| 03B0 | Time - Hour/Minutes of Phase C PF Min | --- | --- | --- | F22 | N/A
| 03B1 | Time - Seconds of Phase C PF Min | --- | --- | --- | F23 | N/A
| 03B2 | Date - Month/Day of Phase C PF Min | --- | --- | --- | F24 | N/A
| 03B3 | Date - Year of Phase C Power Factor Min | --- | --- | --- | F25 | N/A
| 03B4 | Time - Hour/Min of Phase C Real Pwr Max | --- | --- | --- | F22 | N/A
| 03B5 | Time - Seconds of Phase C Real Pwr Max | --- | --- | --- | F23 | N/A
| 03B6 | Date - Month/Day of Phase C Real Pwr Max | --- | --- | --- | F24 | N/A
| 03B7 | Date - Year of Phase C Real Power Max | --- | --- | --- | F25 | N/A
| 03B8 | Time - Hour/Min of Phase C React Pwr Max | --- | --- | --- | F22 | N/A
| 03B9 | Time - Seconds of Phase C React Pwr Max | --- | --- | --- | F23 | N/A
| 03BA | Date - Mnth/Day of Phase C React Pwr Max | --- | --- | --- | F24 | N/A
| 03BB | Date - Year of Phase C Reactive Pwr Max | --- | --- | --- | F25 | N/A
| 03BC | Time - Hour/Min of Phase C App Pwr Max | --- | --- | --- | F22 | N/A
POWER continued | 03BD | Time - Seconds of Phase C App Pwr Max | --- | --- | --- | F23 | N/A
| 03BE | Date - Month/Day of Phase C App Pwr Max | --- | --- | --- | F24 | N/A
| 03BF | Date - Year of Phase C Apparent Pwr Max | --- | --- | --- | F25 | N/A
| 03C0 | Time - Hour/Minutes of Phase C PF Max | --- | --- | --- | F22 | N/A
| 03C1 | Time - Seconds of Phase C PF Max | --- | --- | --- | F23 | N/A
| 03C2 | Date - Month/Day of Phase C PF Max | --- | --- | --- | F24 | N/A
| 03C3 | Date - Year of Phase C Power Factor Max | --- | --- | --- | F25 | N/A
| 03C4 | Reserved
| to |  |  |  |  |  | 
| 03CF | Reserved
ENERGY | 03D0 | 3 Phase Positive Real Energy Used (high) | --- | --- | kWh | F3 | N/A
| 03D1 | 3 Phase Positive Real Energy Used (low)
| 03D2 | 3 Phase Negative Real Energy Used (high) | --- | --- | kWh | F3 | N/A
| 03D3 | 3 Phase Negative Real Energy Used (low)
| 03D4 | 3 Phase Positive React. Energy Used (high) | --- | --- | kvarh | F3 | N/A
| 03D5 | 3 Phase Positive React. Energy Used (low)
| 03D6 | 3 Phase Neg Reactive Energy Used (high) | --- | --- | kvarh | F3 | N/A
| 03D7 | 3 Phase Neg Reactive Energy Used (low)
| 03D8 | 3 Phase Apparent Energy Used (high) | --- | --- | kVAh | F3 | N/A
| 03D9 | 3 Phase Apparent Energy Used (low)
| 03DA | 3 Phase Energy Used in Last 24 h (high) | --- | --- | kWh | F3 | N/A
| 03DB | 3 Phase Energy Used in Last 24 h (low)
| 03DC | 3 Phase Energy Cost Since Reset (high) | --- | --- | $ x 0.01 | F3 | N/A
| 03DD | 3 Phase Energy Cost Since Reset (low)
| 03DE | 3 Phase Energy Cost Per Day (high) | --- | --- | $ x 0.01 | F3 | N/A
| 03DF | 3 Phase Energy Cost Per Day (low)
| 3 | Time - Hours/Minutes of Last Reset | --- | --- | --- | F22 | N/A
| 30 | Time - Seconds of Last Reset | --- | --- | --- | F23 | N/A
| 300 | Date - Month/Day of Last Reset | --- | --- | --- | F24 | N/A
| 3000 | Date - Year of Last Reset | --- | --- | --- | F25 | N/A
| 30000 | Tariff Period 1 Positive Real Energy (high) | --- | --- | kWh | F3 | N/A
| 300000 | Tariff Period 1 Positive Real Energy (low)
| 3000000 | Tariff Period 1 Negative Real Energy (high) | --- | --- | kWh | F3 | N/A
| 30000000 | Tariff Period 1 Negative Real Energy (low)
| 300000000 | Tariff Period 2 Positive Real Energy (high) | --- | --- | kWh | F3 | N/A
| 3000000000 | Tariff Period 2 Positive Real Energy (low)
ENERGY continued | 03EA | Tariff Period 2 Negative Real Energy (high) | --- | --- | kWh | F3 | N/A
| 03EB | Tariff Period 2 Negative Real Energy (low)
| 03EC | Tariff Period 3 Positive Real Energy (high) | --- | --- | kWh | F3 | N/A
| 03ED | Tariff Period 3 Positive Real Energy (low)
| 03EE | Tariff Period 3 Negative Real Energy (high) | --- | --- | kWh | F3 | N/A
| 03EF | Tariff Period 3 Negative Real Energy (low)
| 03F0 | Tariff Period 1 Cost (high) | --- | --- | $ x 0.01 | F3 | N/A
| 03F1 | Tariff Period 1 Cost (low)
| 03F2 | Tariff Period 2 Cost (high) | --- | --- | $ x 0.01 | F3 | N/A
| 03F3 | Tariff Period 2 Cost (low)
| 03F4 | Tariff Period 3 Cost (high) | --- | --- | $ x 0.01 | F3 | N/A
| 03F5 | Tariff Period 3 Cost (low)
| 03F6 | Tariff Period 1 Net Energy Used (high) | --- | --- | kWh | F3 | N/A
| 03F7 | Tariff Period 1 Net Energy Used (low)
| 03F8 | Tariff Period 2 Net Energy Used (high) | --- | --- | kWh | F3 | N/A
| 03F9 | Tariff Period 2 Net Energy Used (low)
| 03FA | Tariff Period 3 Net Energy Used (high) | --- | --- | kWh | F3 | N/A
| 03FB | Tariff Period 3 Net Energy Used (low)
| 03FC | Reserved
| to |  |  |  |  |  | 
| 03FF | Reserved
DEMAND | 400 | Phase A Current Demand | --- | --- | A | F1 | N/A
| 401 | Phase B Current Demand | --- | --- | A | F1 | N/A
| 402 | Phase C Current Demand | --- | --- | A | F1 | N/A
| 403 | Neutral Current Demand | --- | --- | A | F1 | N/A
| 404 | 3 Phase Real Power Demand (high) | --- | --- | 0.01 x kW | F4 | N/A
| 405 | 3 Phase Real Power Demand (low)
| 406 | 3 Phase React Power Demand (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 407 | 3 Phase React Power Demand (low)
| 408 | 3 Phase Apparent Power Demand (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 409 | 3 Phase Apparent Power Demand (low)
| 040A | Phase A Current Demand - Maximum | --- | --- | A | F1 | N/A
| 040B | Phase B Current Demand - Maximum | --- | --- | A | F1 | N/A
| 040C | Phase C Current Demand - Maximum | --- | --- | A | F1 | N/A
| 040D | Neutral Current Demand - Maximum | --- | --- | A | F1 | N/A
| 040E | 3 Phase Real Power Dmd (high) - Max | --- | --- | 0.01 x kW | F4 | N/A
| 040F | 3 Phase Real Power Dmd (low) - Max
| 410 | 3 Phase React Power Dmd (high) - Max | --- | --- | 0.01 x kvar | F4 | N/A
| 411 | 3 Phase React Power Dmd (low) - Max
| 412 | 3 Phase Apparent Power Dmd (high) - Max | --- | --- | 0.01 x kVA | F3 | N/A
| 413 | 3 Phase Apparent Power Dmd (low) - Max
| 414 | Time - Hours/Min of Phase A Cur. Dmd Max | --- | --- | --- | F22 | N/A
DEMAND continued | 415 | Time - Seconds of Phase A Cur. Dmd Max | --- | --- | --- | F23 | N/A
| 416 | Date - Mnth/Day of Phase A Cur. Dmd Max | --- | --- | --- | F24 | N/A
| 417 | Date - Year of Phase A Cur. Dmd Max | --- | --- | --- | F25 | N/A
| 418 | Time - Hours/Min of Phase B Cur. Dmd Max | --- | --- | --- | F22 | N/A
| 419 | Time - Seconds of Phase B Cur. Dmd Max | --- | --- | --- | F23 | N/A
| 041A | Date - Mnth/Day of Phase B Cur. Dmd Max | --- | --- | --- | F24 | N/A
| 041B | Date - Year of Phase B Cur. Dmd Max | --- | --- | --- | F25 | N/A
| 041C | Time - Hours/Min of Phase C Cur. Dmd Max | --- | --- | --- | F22 | N/A
| 041D | Time - Seconds of Phase C Cur. Dmd Max | --- | --- | --- | F23 | N/A
| 041E | Date - Mnth/Day of Phase C Cur. Dmd Max | --- | --- | --- | F24 | N/A
| 041F | Date - Year of Phase C Cur. Dmd Max | --- | --- | --- | F25 | N/A
| 420 | Time - Hours/Min of Neutral Cur. Dmd Max | --- | --- | --- | F22 | N/A
| 421 | Time - Seconds of Neutral Cur. Dmd Max | --- | --- | --- | F23 | N/A
| 422 | Date - Month/Day of Neutral Cur. Dmd Max | --- | --- | --- | F24 | N/A
| 423 | Date - Year of Neutral Cur. Dmd Max | --- | --- | --- | F25 | N/A
| 424 | Time - Hours/Min of Real Pwr Dmd Max | --- | --- | --- | F22 | N/A
| 425 | Time - Seconds of Real Pwr Dmd Max | --- | --- | --- | F23 | N/A
| 426 | Date - Month/Day of Real Pwr Dmd Max | --- | --- | --- | F24 | N/A
| 427 | Date - Year of Real Pwr Dmd Max | --- | --- | --- | F25 | N/A
| 428 | Time - Hours/Min of React Pwr Dmd Max | --- | --- | --- | F22 | N/A
| 429 | Time - Seconds of React Pwr Dmd Max | --- | --- | --- | F23 | N/A
| 042A | Date - Month/Day of React Pwr Dmd Max | --- | --- | --- | F24 | N/A
| 042B | Date - Year of React Pwr Dmd Max | --- | --- | --- | F25 | N/A
| 042C | Time - Hour/Min of App. Pwr Dmd Max | --- | --- | --- | F22 | N/A
| 042D | Time - Seconds of Apparent Pwr Dmd Max | --- | --- | --- | F23 | N/A
| 042E | Date - Month/Day of App. Pwr Dmd Max | --- | --- | --- | F24 | N/A
| 042F | Date - Year of Apparent Pwr Dmd Max | --- | --- | --- | F25 | N/A
| 430 | Reserved
| to |  |  |  |  |  | 
| 043F | Reserved
FREQUENCY | 440 | Frequency | --- | --- | 0.01 x Hz | F1 | N/A
| 441 | Frequency Minimum | --- | --- | 0.01 x Hz | F1 | N/A
| 442 | Frequency Maximum | --- | --- | 0.01 x Hz | F1 | N/A
| 443 | Time - Hours/Min of Frequency Max | --- | --- | --- | F22 | N/A
| 444 | Time - Seconds of Frequency Max | --- | --- | --- | F23 | N/A
| 445 | Date - Month/Day of Frequency Max | --- | --- | --- | F24 | N/A
| 446 | Date - Year of Frequency Max | --- | --- | --- | F25 | N/A
| 447 | Time - Hours/Min of Frequency Min | --- | --- | --- | F22 | N/A
FREQUENCY continued | 448 | Time - Seconds of Frequency Min | --- | --- | --- | F23 | N/A
| 449 | Date - Month/Day of Frequency Min | --- | --- | --- | F24 | N/A
| 044A | Date - Year of Frequency Min | --- | --- | --- | F25 | N/A
| 044B | Reserved
| to |  |  |  |  |  | 
| 044F | Reserved
PULSE INPUT COUNTERS | 450 | Pulse Input 1 (high) | --- | --- | --- | F3 | N/A
| 451 | Pulse Input 1 (low)
| 452 | Pulse Input 2 (high) | --- | --- | --- | F3 | N/A
| 453 | Pulse Input 2 (low)
| 454 | Pulse Input 3 (high) | --- | --- | --- | F3 | N/A
| 455 | Pulse Input 3 (low)
| 456 | Pulse Input 4 (high) | --- | --- | --- | F3 | N/A
| 457 | Pulse Input 4 (low)
ANALOG INPUT | 458 | Main/Alternate Analog Input (High) | --- | --- | --- | F3 | N/A
| 459 | Main/Alternate Analog Input (low)
| 045A | Reserved
| to |  |  |  |  |  | 
| 045F | Reserved
PULSE INPUT COUNTERS | 460 | Totalized Pulse Input (high) | --- | --- | --- | F3 | N/A
| 461 | Totalized Pulse Input (low)
| 462 | Pulse Count Cleared Time – Hours/Min | --- | --- | --- | F22 | N/A
| 463 | Pulse Count Cleared Time – Seconds | --- | --- | --- | F23 | N/A
| 464 | Pulse Count Cleared Date – Month/Day | --- | --- | --- | F24 | N/A
| 465 | Pulse Count Cleared Date – Year | --- | --- | --- | F25 | N/A
| 466 | Reserved
| to |  |  |  |  |  | 
| 046F | Reserved
POWER QUALITY | 470 | Ia Crest Factor | --- | --- | 0.001 xCF | F1 | N/A
| 471 | Ib Crest Factor | --- | --- | 0.001 xCF | F1 | N/A
| 472 | Ic Crest Factor | --- | --- | 0.001 xCF | F1 | N/A
| 473 | Ia Transformer Harmonic Derating Factor | --- | --- | 0.01xTHDF | F1 | N/A
| 474 | Ib Transformer Harmonic Derating Factor | --- | --- | 0.01xTHDF | F1 | N/A
| 475 | Ic Transformer Harmonic Derating Factor | --- | --- | 0.01xTHDF | F1 | N/A
| 476 | Reserved
| 477 | Reserved
TOTAL HARMONIC DISTORTION | 478 | Phase A Current THD | --- | --- | 0.1 x % | F1 | N/A
| 479 | Phase B Current THD | --- | --- | 0.1 x % | F1 | N/A
| 047A | Phase C Current THD | --- | --- | 0.1 x % | F1 | N/A
| 047B | Neutral Current THD | --- | --- | 0.1 x % | F1 | N/A
| 047C | Voltage Van THD | --- | --- | 0.1 x % | F1 | N/A
| 047D | Voltage Vbn THD | --- | --- | 0.1 x % | F1 | N/A
| 047E | Voltage Vcn THD | --- | --- | 0.1 x % | F1 | N/A
| 047F | Voltage Vab THD | --- | --- | 0.1 x % | F1 | N/A
| 480 | Voltage Vbc THD | --- | --- | 0.1 x % | F1 | N/A
TOTAL HARMONIC DISTORTION continued | 481 | Reserved
| 482 | Phase A Current THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 483 | Phase B Current THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 484 | Phase C Current THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 485 | Neutral Current THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 486 | Voltage Van THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 487 | Voltage Vbn THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 488 | Voltage Vcn THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 489 | Voltage Vab THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 048A | Voltage Vbc THD - Maximum | --- | --- | 0.1 x % | F1 | N/A
| 048B | Reserved
| 048C | Time - Hour/Min of Phase A Cur. THD Max | --- | --- | --- | F22 | N/A
| 048D | Time - Seconds of Phase A Cur. THD Max | --- | --- | --- | F23 | N/A
| 048E | Date - Mnth/Day of Phase A Cur. THD Max | --- | --- | --- | F24 | N/A
| 048F | Date - Year of Phase A Cur. THD Max | --- | --- | --- | F25 | N/A
| 490 | Time - Hour/Min of Phase B Cur. THD Max | --- | --- | --- | F22 | N/A
| 491 | Time - Seconds of Phase B Cur. THD Max | --- | --- | --- | F23 | N/A
| 492 | Date - Mnth/Day of Phase B Cur. THD Max | --- | --- | --- | F24 | N/A
| 493 | Date - Year of Phase B Cur. THD Max | --- | --- | --- | F25 | N/A
| 494 | Time - Hour/Min of Phase C Cur. THD Max | --- | --- | --- | F22 | N/A
| 495 | Time - Seconds of Phase C Cur. THD Max | --- | --- | --- | F23 | N/A
| 496 | Date - Mnth/Day of Phase C Cur. THD Max | --- | --- | --- | F24 | N/A
POWER QUALITY continued | 497 | Date - Year of Phase C Cur. THD Max | --- | --- | --- | F25 | N/A
| 498 | Time - Hour/Min of Neutral Cur. THD Max | --- | --- | --- | F22 | N/A
| 499 | Time - Seconds of Neutral Cur. THD Max | --- | --- | --- | F23 | N/A
| 049A | Date - Mnth/Day of Neutral Cur. THD Max | --- | --- | --- | F24 | N/A
| 049B | Date - Year of Neutral Cur. THD Max | --- | --- | --- | F25 | N/A
| 049C | Time - Hours/Min of Van THD Max | --- | --- | --- | F22 | N/A
| 049D | Time - Seconds of Van THD Max | --- | --- | --- | F23 | N/A
| 049E | Date - Month/Day of Van THD Max | --- | --- | --- | F24 | N/A
| 049F | Date - Year of Van THD Max | --- | --- | --- | F25 | N/A
| 04A0 | Time - Hours/Min of Vbn THD Max | --- | --- | --- | F22 | N/A
| 04A1 | Time - Seconds of Vbn THD Max | --- | --- | --- | F23 | N/A
| 04A2 | Date - Month/Day of Vbn THD Max | --- | --- | --- | F24 | N/A
| 04A3 | Date - Year of Vbn THD Max | --- | --- | --- | F25 | N/A
| 04A4 | Time - Hours/Min of Vcn THD Max | --- | --- | --- | F22 | N/A
| 04A5 | Time - Seconds of Vcn THD Max | --- | --- | --- | F23 | N/A
| 04A6 | Date - Month/Day of Vcn THD Max | --- | --- | --- | F24 | N/A
| 04A7 | Date - Year of Vcn THD Max | --- | --- | --- | F25 | N/A
TOTAL HARMONIC DISTORTION continued | 04A8 | Time - Hours/Min of Vab THD Max | --- | --- | --- | F22 | N/A
| 04A9 | Time - Seconds of Vab THD Max | --- | --- | --- | F23 | N/A
| 04AA | Date - Month/Day of Vab THD Max | --- | --- | --- | F24 | N/A
| 04AB | Date - Year of Vab THD Max | --- | --- | --- | F25 | N/A
| 04AC | Time - Hours/Min of Vbc THD Max | --- | --- | --- | F22 | N/A
| 04AD | Time - Seconds of Vbc THD Max | --- | --- | --- | F23 | N/A
| 04AE | Date - Month/Day of Vbc THD Max | --- | --- | --- | F24 | N/A
| 04AF | Date - Year of Vbc THD Max | --- | --- | --- | F25 | N/A
| 04B0 | Reserved
| 04B1 | Reserved
| 04B2 | Reserved
| 04B3 | Reserved
| 04B4 | Average Current THD | --- | --- | 0.1 x% | F1 | N/A
| 04B5 | Average Voltage THD | --- | --- | 0.1 x% | F1 | N/A
| 04B6 | Reserved
| to |  |  |  |  |  | 
| 04C7 | Reserved
DEBUG DATA | 04C8 | ADC Reference | --- | --- | --- | F1 | N/A
| 04C9 | Power Loss Fine Time | --- | --- | 10 ms | F1 | N/A
| 04CA | Power Loss Coarse Time | --- | --- | 0.1 min | F1 | N/A
| 04CB | Current Key Press | --- | --- | --- | F6 | N/A
| 04CC | Internal Fault Error Code | --- | --- | --- | F108 | N/A
| 04CD | Reserved
| to |  |  |  |  |  | 
| 04D7 | Reserved
MESSAGE BUFFER | 04D8 | Message Buffer characters 1 and 2 | --- | --- | ASCII | F10 | N/A
| 04D9 | Message Buffer characters 3 and 4 | --- | --- | ASCII | F10 | N/A
| 04DA | Message Buffer characters 5 and 6 | --- | --- | ASCII | F10 | N/A
| 04DB | Message Buffer characters 7 and 8 | --- | --- | ASCII | F10 | N/A
| 04DC | Message Buffer characters 9 and 10 | --- | --- | ASCII | F10 | N/A
| 04DD | Message Buffer characters 11 and 12 | --- | --- | ASCII | F10 | N/A
| 04DE | Message Buffer characters 13 and 14 | --- | --- | ASCII | F10 | N/A
| 04DF | Message Buffer characters 15 and 16 | --- | --- | ASCII | F10 | N/A
| 4 | Message Buffer characters 17 and 18 | --- | --- | ASCII | F10 | N/A
| 40 | Message Buffer characters 19 and 20 | --- | --- | ASCII | F10 | N/A
| 400 | Message Buffer characters 21 and 22 | --- | --- | ASCII | F10 | N/A
| 4000 | Message Buffer characters 23 and 24 | --- | --- | ASCII | F10 | N/A
| 40000 | Message Buffer characters 25 and 26 | --- | --- | ASCII | F10 | N/A
| 400000 | Message Buffer characters 27 and 28 | --- | --- | ASCII | F10 | N/A
| 4000000 | Message Buffer characters 29 and 30 | --- | --- | ASCII | F10 | N/A
| 40000000 | Message Buffer characters 31 and 32 | --- | --- | ASCII | F10 | N/A
| 400000000 | Message Buffer characters 33 and 34 | --- | --- | ASCII | F10 | N/A
| 4000000000 | Message Buffer characters 35 and 36 | --- | --- | ASCII | F10 | N/A
MESSAGE BUFFER continued | 04EA | Message Buffer characters 37 and 38 | --- | --- | ASCII | F10 | N/A
| 04EB | Message Buffer characters 39 and 40 | --- | --- | ASCII | F10 | N/A
| 04EC | Reserved
| to |  |  |  |  |  | 
| 04F7 | Reserved
HIGH SPEED SAMPLES FOR HARMONIC SPECTRUM | 04F8 | High Speed Sampling Parameter | --- | --- | --- | F26 | N/A
| 04F9 | High Speed Sampling Scale Factor (high) li | --- | --- | A or V x 10000 | F3 | N/A
| 04FA | High Speed Samp ng Scale Factor (low)
| 04FB | Freq. of High Speed Sampling Waveform | --- | --- | 0.01 xHz | F1 | N/A
| 04FC | Time - Hours/Minutes of Last Sampling | --- | --- | --- | F22 | N/A
| 04FD | Time - Seconds of Last Sampling | --- | --- | --- | F23 | N/A
| 04FE | Date - Month/Day of Last Sampling | --- | --- | --- | F24 | N/A
| 04FF | Date - Year of Last Sampling | --- | --- | --- | F25 | N/A
| 500 | High Speed Sample Buffer 1 | --- | --- | ADC counts | F2 | N/A
| 501 | High Speed Sample Buffer 2 | --- | --- | ADC counts | F2 | N/A
| 502 | High Speed Sample Buffer 3 | --- | --- | ADC counts | F2 | N/A
| 503 | High Speed Sample Buffer 4 | --- | --- | ADC counts | F2 | N/A
| to |  |  |  |  |  | 
| 05FD | High Speed Sample Buffer 254 | --- | --- | ADC counts | F2 | N/A
| 05FE | High Speed Sample Buffer 255 | --- | --- | ADC counts | F2 | N/A
| 05FF | High Speed Sample Buffer 256 | --- | --- | ADC counts | F2 | N/A
| 600 | Reserved
| to |  |  |  |  |  | 
| 061F | Reserved
WAVEFORM CAPTURE HEADER | 620 | Time - Hours/Minutes of Last Capture | --- | --- | --- | F22 | N/A
| 621 | Time - Seconds of Last Capture | --- | --- | --- | F23 | N/A
| 622 | Date - Month/Day of Last Capture | --- | --- | --- | F24 | N/A
| 623 | Date - Year of Last Capture | --- | --- | --- | F25 | N/A
| 624 | Frequency of Last Capture | --- | --- | 0.01 x Hz | F1 | N/A
| 625 | Reserved
| 626 | Reserved
| 627 | Reserved
WAVEFORM CAPTURE Ia | 628 | Ia Waveform Capture Scale Factor (high) | --- | --- | A x 10000 | F3 | N/A
| 629 | Ia Waveform Capture Scale Factor (low)
| 062A | Ia Sample Buffer 1 | --- | --- | ADC counts | F2 | N/A
| 062B | Ia Sample Buffer 2 | --- | --- | ADC counts | F2 | N/A
| 062C | Ia Sample Buffer 3 | --- | --- | ADC counts | F2 | N/A
| 062D | Ia Sample Buffer 4 | --- | --- | ADC counts | F2 | N/A
| to |  |  |  |  |  | 
| 06A6 | Ia Sample Buffer 125 | --- | --- | ADC counts | F2 | N/A
| 06A7 | Ia Sample Buffer 126 | --- | --- | ADC counts | F2 | N/A
| 06A8 | Ia Sample Buffer 127 | --- | --- | ADC counts | F2 | N/A
| 06A9 | Ia Sample Buffer 128 | --- | --- | ADC counts | F2 | N/A
WAVEFORM CAPTURE Ia continued | 06AA | Reserved
| to |  |  |  |  |  | 
| 06AF | Reserved
WAVEFORM CAPTURE Ib | 06B0 | Ib Waveform Capture Scale Factor (high) | --- | --- | A x 10000 | F3 | N/A
| 06B1 | Ib Waveform Capture Scale Factor (low)
| 06B2 | Ib Sample Buffer 1 | --- | --- | ADC counts | F2 | N/A
| 06B3 | Ib Sample Buffer 2 | --- | --- | ADC counts | F2 | N/A
| 06B4 | Ib Sample Buffer 3 | --- | --- | ADC counts | F2 | N/A
| 06B5 | Ib Sample Buffer 4 | --- | --- | ADC counts | F2 | N/A
| to |  |  |  |  |  | 
| 072E | Ib Sample Buffer 125 | --- | --- | ADC counts | F2 | N/A
| 072F | Ib Sample Buffer 126 | --- | --- | ADC counts | F2 | N/A
| 730 | Ib Sample Buffer 127 | --- | --- | ADC counts | F2 | N/A
| 731 | Ib Sample Buffer 128 | --- | --- | ADC counts | F2 | N/A
| 732 | Reserved
| to |  |  |  |  |  | 
| 737 | Reserved
WAVEFORM CAPTURE Ic | 738 | Ic Waveform Capture Scale Factor (high) | --- | --- | A x 10000 | F3 | N/A
| 739 | Ic Waveform Capture Scale Factor (low)
| 073A | Ic Sample Buffer 1 | --- | --- | ADC counts | F2 | N/A
| 073B | Ic Sample Buffer 2 | --- | --- | ADC counts | F2 | N/A
| 073C | Ic Sample Buffer 3 | --- | --- | ADC counts | F2 | N/A
| 073D | Ic Sample Buffer 4 | --- | --- | ADC counts | F2 | N/A
| to |  |  |  |  |  | 
| 07B6 | Ic Sample Buffer 125 | --- | --- | ADC counts | F2 | N/A
| 07B7 | Ic Sample Buffer 126 | --- | --- | ADC counts | F2 | N/A
| 07B8 | Ic Sample Buffer 127 | --- | --- | ADC counts | F2 | N/A
| 07B9 | Ic Sample Buffer 128 | --- | --- | ADC counts | F2 | N/A
| 07BA | Reserved
| to |  |  |  |  |  | 
| 07BF | Reserved
WAVEFORM CAPTURE In | 07C0 | In Waveform Capture Scale Factor (high) | --- | --- | A x 10000 | F3 | N/A
| 07C1 | In Waveform Capture Scale Factor (low)
| 07C2 | In Sample Buffer 1 | --- | --- | ADC counts | F2 | N/A
| 07C3 | In Sample Buffer 2 | --- | --- | ADC counts | F2 | N/A
| 07C4 | In Sample Buffer 3 | --- | --- | ADC counts | F2 | N/A
| 07C5 | In Sample Buffer 4 | --- | --- | ADC counts | F2 | N/A
| to |  |  |  |  |  | 
| 083E | In Sample Buffer 125 | --- | --- | ADC counts | F2 | N/A
| 083F | In Sample Buffer 126 | --- | --- | ADC counts | F2 | N/A
| 840 | In Sample Buffer 127 | --- | --- | ADC counts | F2 | N/A
| 841 | In Sample Buffer 128 | --- | --- | ADC counts | F2 | N/A
| 842 | Reserved
| to |  |  |  |  |  | 
| 847 | Reserved
WAVEFORM CAPTURE Van | 848 | Van Waveform Capture Scale Factor (high) | --- | --- | V x 10000 | F3 | N/A
| 849 | Van Waveform Capture Scale Factor (low)
| 084A | Van Sample Buffer 1 | --- | --- | ADC counts | F2 | N/A
| 084B | Van Sample Buffer 2 | --- | --- | ADC counts | F2 | N/A
| 084C | Van Sample Buffer 3 | --- | --- | ADC counts | F2 | N/A
| 084D | Van Sample Buffer 4 | --- | --- | ADC counts | F2 | N/A
| to |  |  |  |  |  | 
| 08C6 | Van Sample Buffer 125 | --- | --- | ADC counts | F2 | N/A
| 08C7 | Van Sample Buffer 126 | --- | --- | ADC counts | F2 | N/A
| 08C8 | Van Sample Buffer 127 | --- | --- | ADC counts | F2 | N/A
| 08C9 | Van Sample Buffer 128 | --- | --- | ADC counts | F2 | N/A
| 08CA | Reserved
| to |  |  |  |  |  | 
| 08CF | Reserved
WAVEFORM CAPTURE Vbn | 08D0 | Vbn Waveform Capture Scale Factor (high) | --- | --- | V x 10000 | F3 | N/A
| 08D1 | Vbn Waveform Capture Scale Factor (low)
| 08D2 | Vbn Sample Buffer 1 | --- | --- | ADC counts | F2 | N/A
| 08D3 | Vbn Sample Buffer 2 | --- | --- | ADC counts | F2 | N/A
| 08D4 | Vbn Sample Buffer 3 | --- | --- | ADC counts | F2 | N/A
| 08D5 | Vbn Sample Buffer 4 | --- | --- | ADC counts | F2 | N/A
| to |  |  |  |  |  | 
| 094E | Vbn Sample Buffer 125 | --- | --- | ADC counts | F2 | N/A
| 094F | Vbn Sample Buffer 126 | --- | --- | ADC counts | F2 | N/A
| 950 | Vbn Sample Buffer 127 | --- | --- | ADC counts | F2 | N/A
| 951 | Vbn Sample Buffer 128 | --- | --- | ADC counts | F2 | N/A
| 952 | Reserved
| to |  |  |  |  |  | 
| 957 | Reserved
WAVEFORM CAPTURE Vcn | 958 | Vcn Waveform Capture Scale Factor (high) | --- | --- | V x 10000 | F3 | N/A
| 959 | Vcn Waveform Capture Scale Factor (low)
| 095A | Vcn Sample Buffer 1 | --- | --- | ADC counts | F2 | N/A
| 095B | Vcn Sample Buffer 2 | --- | --- | ADC counts | F2 | N/A
| 095C | Vcn Sample Buffer 3 | --- | --- | ADC counts | F2 | N/A
| 095D | Vcn Sample Buffer 4 | --- | --- | ADC counts | F2 | N/A
| to |  |  |  |  |  | 
| 09D6 | Vcn Sample Buffer 125 | --- | --- | ADC counts | F2 | N/A
| 09D7 | Vcn Sample Buffer 126 | --- | --- | ADC counts | F2 | N/A
| 09D8 | Vcn Sample Buffer 127 | --- | --- | ADC counts | F2 | N/A
| 09D9 | Vcn Sample Buffer 128 | --- | --- | ADC counts | F2 | N/A
WAVEFORM CAPTURE Vcn continued | 09DA | Reserved
| to |  |  |  |  |  | 
| 09FF | Reserved
DATA LOGGER DATA | 0A00 | Data Log Memory Access Block Number | --- | --- | --- | F1 | 0
| 0A01 | Data Log Register 0 | --- | --- | --- | F1 | ---
| 0A02 | Data Log Register 1 | --- | --- | --- | F1 | ---
| 0A03 | Data Log Register 2 | --- | --- | --- | F1 | ---
| 0A04 | Data Log Register 3 | --- | --- | --- | F1 | ---
| to |  |  |  |  |  | 
| 0A3D | Data Log Register 60 | --- | --- | --- | F1 | ---
| 0A3E | Data Log Register 61 | --- | --- | --- | F1 | ---
| 0A3F | Data Log Register 62 | --- | --- | --- | F1 | ---
| 0A40 | Data Log Register 63 | --- | --- | --- | F1 | ---
| 0A41 | Reserved
| to |  |  |  |  |  | 
| 0A4F | Reserved
DATA LOGGER LOG NUMBERS | 0A50 | Ia Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A51 | Ib Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A52 | Ic Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A53 | Iavg Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A54 | In Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A55 | I Unbalance Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A56 | Van Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A57 | Vbn Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A58 | Vcn Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A59 | Vpavg Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A5A | Vab Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A5B | Vbc Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A5C | Vca Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A5D | Vlavg Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A5E | V Unbalance Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A5F | Pa Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A60 | Qa Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A61 | Sa Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A62 | PFa Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A63 | Pb Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A64 | Qb Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A65 | Sb Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A66 | PFb Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A67 | Pc Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A68 | Qc Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A69 | Sc Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A6A | PFc Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A6B | P3 Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A6C | Q3 Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A6D | S3 Log Number | --- | --- | --- | F110 | 0 = not selected
DATA LOGGER LOG NUMBERS continued | 0A6E | PF3 Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A6F | Frequency Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A70 | Positive kWh Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A71 | Negative kWh Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A72 | Positive kvarh Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A73 | Negative kvarh Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A74 | kVAh Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A75 | Ia Demand Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A76 | Ib Demand Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A77 | Ic Demand Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A78 | In Demand Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A79 | P3 Demand Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A7A | Q3 Demand Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A7B | S3 Demand Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A7C | Ia THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A7D | Ib THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A7E | Ic THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A7F | In THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A80 | Van THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A81 | Vbn THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A82 | Vcn THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A83 | Vab THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A84 | Vbc THD Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A85 | Analog Input Log Number | --- | --- | --- | F110 | 0 = not selected
| 0A86 | Reserved
| to |  |  |  |  |  | 
| 0A8F | Reserved
DATA LOGGER LOG 1 HEADER | 0A90 | Log 1 Time Interval (high) | --- | --- | s | F3 | N/A
| 0A91 | Log 1 Time Interval (low)
| 0A92 | Log 1 Time - Hours/Minutes | --- | --- | --- | F22 | N/A
| 0A93 | Log 1 Time - Seconds | --- | --- | --- | F23 | N/A
| 0A94 | Log 1 Date - Month/Day | --- | --- | --- | F24 | N/A
| 0A95 | Log 1 Date - Year | --- | --- | --- | F25 | N/A
| 0A96 | Log 1 Start Block Number | --- | --- | --- | F1 | 0
| 0A97 | Log 1 Start Register Number | --- | --- | --- | F1 | 0
| 0A98 | Log 1 Record Size | --- | --- | bytes | F1 | 0
| 0A99 | Log 1 Total Records (high) |  |  |  | F3
| 0A9A | Log 1 Total Records (low)
| 0A9B | Log 1 Block Number of First Record |  |  |  | F1
| 0A9C | Log 1 Register Number of First Record |  |  |  | F1
| 0A9D | Log 1 Pointer to 1st Item of 1st Rec. (high) | --- | --- | --- | F1 | 0
| 0A9E | Log 1 Pointer to 1st Item of 1st Record (low) | --- | --- | --- | F1 | 0
| 0A9F | Log 1 Block Number of Next Record to Write |  |  |  | F1
| 0AA0 | Log 1 Register No. of Next Record to Write |  |  |  | F1
DATA LOGGER LOG 1 HEADER continued | 0AA1 | Log 1 Pointer of 1st Item of Record after Last (high) |  |  |  | F3
| 0AA2 | Log 1 Pointer of 1st Item of Record after Last (low)
| 0AA3 | Log 1 Status | --- | --- | --- | F35 | 0 = STOPPED
| 0AA4 | Log 1 Records Used (high) |  |  |  | F3
| 0AA5 | Log 1 Records Used (low)
| 0AA6 | Log 1 Time Until next Reading (high) | --- | --- | s | F3 | N/A
| 0AA7 | Log 1 Time Until next Reading (low)
| 0AA8 | Reserved
| to |  |  |  |  |  | 
| 0AAB | Reserved
DATA LOGGER LOG 2 HEADER | 0AAC | Log 2 Time Interval (high) | --- | --- | s | F3 | N/A
| 0AAD | Log 2 Time Interval (low)
| 0AAE | Log 2 Time - Hours/Minutes | --- | --- | --- | F22 | N/A
| 0AAF | Log 2 Time - Seconds | --- | --- | --- | F23 | N/A
| 0AB0 | Log 2 Date - Month/Day | --- | --- | --- | F24 | N/A
| 0AB1 | Log 2 Date - Year | --- | --- | --- | F25 | N/A
| 0AB2 | Log 2 Start Block Number | --- | --- | --- | F1 | 0
| 0AB3 | Log 2 Start Register Number | --- | --- | --- | F1 | 0
| 0AB4 | Log 2 Record Size | --- | --- | bytes | F1 | 0
| 0AB5 | Log 2 Total Records (high) |  |  |  | F3
| 0AB6 | Log 2 Total Records (low)
| 0AB7 | Log 2 Block Number of First Record |  |  |  | F1
| 0AB8 | Log 2 Register Number of First Record |  |  |  | F1
| 0AB9 | Log 2 Pointer to 1st Item of 1st Rec. (high) | --- | --- | --- | F1 | 0
| 0ABA | Log 2 Pointer to 1st Item of 1st Record (low) | --- | --- | --- | F1 | 0
| 0ABB | Log 2 Block Number of Next Record to Write |  |  |  | F1
| 0ABC | Log 2 Register No. of Next Record to Write |  |  |  | F1
| 0ABD | Log 2 Pointer of 1st Item of Record after Last (high) |  |  |  | F3
| 0ABE | Log 2 Pointer of 1st Item of Record after Last (low)
| 0ABF | Log 2 Status | --- | --- | --- | F35 | 0 = STOPPED
| 0AC0 | Log 2 Records Used (high) |  |  |  | F3
| 0AC1 | Log 2 Records Used (low)
| 0AC2 | Log 2 Time Until next Reading (high) | --- | --- | s | F3 | N/A
| 0AC3 | Log 2 Time Until next Reading (low)
| 0AC4 | Reserved
| to |  |  |  |  |  | 
| 0ACF | Reserved
EVENT RECORD | 0AD0 | Total Number of Events Since Last Clear | --- | --- | --- | F1 | 0
| 0AD1 | Event Record Last Cleared Time - Hrs./ Min. | --- | --- | --- | F22 | N/A
| 0AD2 | Event Record Last Cleared Time - Seconds | --- | --- | --- | F23 | N/A
| 0AD3 | Event Record Last Cleared Date - Month/Day | --- | --- | --- | F24 | N/A
EVENT RECORD continued | 0AD4 | Event Record Last Cleared Date - Year | --- | --- | --- | F25 | N/A
| 0AD5 | Reserved
| to |  |  |  |  |  | 
| 0ADF | Reserved
| 0AE0 | Record #N Event Number | --- | --- | --- | F1 | N/A
| 0AE1 | Record #N Event Cause | --- | --- | --- | F36 | 0 = NO EVENT
| 0AE2 | Record #N Time - Hours/Minutes | --- | --- | --- | F22 | N/A
| 0AE3 | Record #N Time - Seconds | --- | --- | --- | F23 | N/A
| 0AE4 | Record #N Date - Month/Day | --- | --- | --- | F24 | N/A
| 0AE5 | Record #N Date - Year | --- | --- | --- | F25 | N/A
| 0AE6 | Record #N Switches and Relays States | --- | --- | --- | F111 | N/A
| 0AE7 | Record #N Ia | --- | --- | A | F1 | N/A
| 0AE8 | Record #N Ib | --- | --- | A | F1 | N/A
| 0AE9 | Record #N Ic | --- | --- | A | F1 | N/A
| 0AEA | Record #N In | --- | --- | A | F1 | N/A
| 0AEB | Record #N I Unbalance | --- | --- | 0.1 x% | F1 | N/A
| 0AEC | Record #N Van (high) | --- | --- | V | F3 | N/A
| 0AED | Record #N Van (low)
| 0AEE | Record #N Vbn (high) | --- | --- | V | F3 | N/A
| 0AEF | Record #N Vbn (low)
| 0AF0 | Record #N Vcn (high) | --- | --- | V | F3 | N/A
| 0AF1 | Record #N Vcn (low)
| 0AF2 | Record #N Vab (high) | --- | --- | V | F3 | N/A
| 0AF3 | Record #N Vab (low)
| 0AF4 | Record #N Vbc (high) | --- | --- | V | F3 | N/A
| 0AF5 | Record #N Vbc (low)
| 0AF6 | Record #N Vca (high) | --- | --- | V | F3 | N/A
| 0AF7 | Record #N Vca (low)
| 0AF8 | Record #N V Unbalance | --- | --- | 0.1 x% | F1 | N/A
| 0AF9 | Record #N Pa (high) | --- | --- | 0.01 x kW | F4 | N/A
| 0AFA | Record #N Pa (low)
| 0AFB | Record #N Qa (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 0AFC | Record #N Qa (low)
| 0AFD | Record #N Sa (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 0AFE | Record #N Sa (low)
| 0AFF | Record #N PFa | --- | --- | 0.01 x PF | F2 | N/A
| 0B00 | Record #N Pb (high) | --- | --- | 0.01 x kW | F4 | N/A
| 0B01 | Record #N Pb (low)
| 0B02 | Record #N Qb (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 0B03 | Record #N Qb (low)
| 0B04 | Record #N Sb (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 0B05 | Record #N Sb (low)
| 0B06 | Record #N PFb | --- | --- | 0.01 x PF | F2 | N/A
| 0B07 | Record #N Pc (high) | --- | --- | 0.01 x kW | F4 | N/A
| 0B08 | Record #N Pc (low)
EVENT RECORD continued | 0B09 | Record #N Qc (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 0B0A | Record #N Qc (low)
| 0B0B | Record #N Sc (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 0B0C | Record #N Sc (low)
| 0B0D | Record #N PFc | --- | --- | 0.01 x PF | F2 | N/A
| 0B0E | Record #N P3 (high) | --- | --- | 0.01 x kW | F4 | N/A
| 0B0F | Record #N P3 (low)
| 0B10 | Record #N Q3 (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 0B11 | Record #N Q3 (low)
| 0B12 | Record #N S3 (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 0B13 | Record #N S3 (low)
| 0B14 | Record #N PF3 | --- | --- | 0.01 x PF | F2 | N/A
| 0B15 | Record #N Frequency | --- | --- | 0.01 x Hz | F1 | N/A
| 0B16 | Record #N Positive kWh (high) | --- | --- | kWh | F3 | N/A
| 0B17 | Record #N Positive kWh (low)
| 0B18 | Record #N Negative kWh (high) | --- | --- | kWh | F3 | N/A
| 0B19 | Record #N Negative kWh (low)
| 0B1A | Record #N Positive kvarh (high) | --- | --- | kvarh | F3 | N/A
| 0B1B | Record #N Positive kvarh (low)
| 0B1C | Record #N Negative kvarh (high) | --- | --- | kvarh | F3 | N/A
| 0B1D | Record #N Negative kvarh (low)
| 0B1E | Record #N kVAh (high) | --- | --- | kVAh | F3 | N/A
| 0B1F | Record #N kVAh (low)
| 0B20 | Record #N Ia Demand | --- | --- | A | F1 | N/A
| 0B21 | Record #N Ib Demand | --- | --- | A | F1 | N/A
| 0B22 | Record #N Ic Demand | --- | --- | A | F1 | N/A
| 0B23 | Record #N In Demand | --- | --- | A | F1 | N/A
| 0B24 | Record #N P3 Demand (high) | --- | --- | 0.01 x kW | F4 | N/A
| 0B25 | Record #N P3 Demand (low)
| 0B26 | Record #N Q3 Demand (high) | --- | --- | 0.01 x kvar | F4 | N/A
| 0B27 | Record #N Q3 Demand (low)
| 0B28 | Record #N S3 Demand (high) | --- | --- | 0.01 x kVA | F3 | N/A
| 0B29 | Record #N S3 Demand (low)
| 0B2A | Record #N Ia THD | --- | --- | 0.1 x % | F1 | N/A
| 0B2B | Record #N Ib THD | --- | --- | 0.1 x % | F1 | N/A
| 0B2C | Record #N Ic THD | --- | --- | 0.1 x % | F1 | N/A
| 0B2D | Record #N In THD | --- | --- | 0.1 x % | F1 | N/A
| 0B2E | Record #N Van THD | --- | --- | 0.1 x % | F1 | N/A
| 0B2F | Record #N Vbn THD | --- | --- | 0.1 x % | F1 | N/A
| 0B30 | Record #N Vcn THD | --- | --- | 0.1 x % | F1 | N/A
| 0B31 | Record #N Vab THD | --- | --- | 0.1 x % | F1 | N/A
| 0B32 | Record #N Vbc THD | --- | --- | 0.1 x % | F1 | N/A
| 0B33 | Record #N Analog Input (high) | --- | --- | --- | F3 | N/A
| 0B34 | Record #N Analog Input (low)
| 0B35 | Record #N Trace Memory Trigger Cause | --- | --- | --- | F41 | N/A
| 0B36 | Record #N Internal Fault Error Code | --- | --- | --- | F108 | N/A
EVENT RECORD continued | 0B37 | Reserved
| to |  |  |  |  |  | 
| 0B7F | Reserved
TRACE MEMORY | 0B80 | Trace Memory Usage | --- | --- | --- | F37 | N/A
| 0B81 | Trace Memory Trigger Flag | --- | --- | --- | F113 | N/A
| 0B82 | Trace Memory Trigger Counter | --- | --- | --- | F1 | N/A
| 0B83 | Total Trace Memory Triggers | --- | --- | --- | F1 | N/A
| 0B88 | Trigger Cause - Trace 1 | --- | --- | --- | F41 | N/A
| 0B89 | Time - Hours/Minutes - Trace 1 | --- | --- | --- | F22 | N/A
| 0B8A | Time - Seconds - Trace 1 | --- | --- | --- | F23 | N/A
| 0B8B | Date - Month/Day - Trace 1 | --- | --- | --- | F24 | N/A
| 0B8C | Date - Year - Trace 1 | --- | --- | --- | F25 | N/A
| 0B8D | Trigger Sample Number 1 | --- | --- | --- | F1 | N/A
| 0B8E | Frequency 1 | --- | --- | 0.01 x Hz | F1 | N/A
| 0B98 | Trigger Cause - Trace 2 | --- | --- | --- | F41 | N/A
| 0B99 | Time - Hours/Minutes - Trace 2 | --- | --- | --- | F22 | N/A
| 0B9A | Time - Seconds - Trace 2 | --- | --- | --- | F23 | N/A
| 0B9B | Date - Month/Day - Trace 2 | --- | --- | --- | F24 | N/A
| 0B9C | Date - Year - Trace 2 | --- | --- | --- | F25 | N/A
| 0B9D | Trigger Sample Number 2 | --- | --- | --- | F1 | N/A
| 0B9E | Frequency 2 | --- | --- | 0.01 x Hz | F1 | N/A
| 0BA8 | Trigger Cause - Trace 3 | --- | --- | --- | F41 | N/A
| 0BA9 | Time - Hours/Minutes - Trace 3 | --- | --- | --- | F22 | N/A
| 0BAA | Time - Seconds - Trace 3 | --- | --- | --- | F23 | N/A
| 0BAB | Date - Month/Day - Trace 3 | --- | --- | --- | F24 | N/A
| 0BAC | Date - Year - Trace 3 | --- | --- | --- | F25 | N/A
| 0BAD | Trigger Sample Number 3 | --- | --- | --- | F1 | N/A
| 0BAE | Frequency 3 | --- | --- | 0.01xHz | F1 | N/A
| 0BB8 | Trace Memory Waveform Selection | --- | --- | --- | F40 | N/A
| 0BB9 | Waveform Scale Factor (high) | --- | --- | A/Vx10000 | F3 | N/A
| 0BBA | Waveform Scale Factor (low)
| 0BBB | Data Buffer 1 | --- | --- | ADCcounts/2 | F2 | N/A
| 0BBC | Data Buffer 2 | --- | --- | ADCcounts/2 | F2 | N/A
| to |  |  |  |  |  | 
| 0DF9 | Data Buffer 575 | --- | --- | ADCcounts/2 | F2 | N/A
| 0DFA | Data Buffer 576 | --- | --- | ADCcounts/2 | F2 | N/A
| 0DFB | Reserved
| to |  |  |  |  |  | 
| 0DFF | Reserved
| 0 | Invalid Serial Number Flag | --- | --- | --- | F117 | N/A
| 0 | Reserved
| to |  |  |  |  |  | 
| 0E1F | Reserved
VOLTAGE DISTUR- BANCE RECORDER | 0 | Disturbances since Last Clear | --- | --- | --- | F1 | 0
| 0 | Swell/Sag Last Cleared Time (Hrs./Min.) | --- | --- | --- | F22 | N/A
| 0 | Swell/Sag Last Cleared Time (Sec.) | --- | --- | --- | F23 | N/A
| 0 | Swell/Sag Last Cleared Date (Month/ Day.) | --- | --- | --- | F24 | N/A
| 0 | Swell/Sag Last Cleared Date (Year.) | --- | --- | --- | F25 | N/A
| 0 | Reserved
| to |  |  |  |  |  | 
| 0E2F | Reserved
| 0 | Record N Disturbance Number |  |  |  | F1 | N/A
| 0 | Record N Disturbance Type |  |  |  | F118 | N/A
| 0 | Record N Disturbance Source |  |  |  | F119 | N/A
| 0 | Record N Time (hours/minutes) |  |  |  | F22 | N/A
| 0 | Record N Time (seconds) |  |  |  | F23 | N/A
| 0 | Record N Date (month/day) |  |  |  | F24 | N/A
| 0 | Record N Date (seconds) |  |  |  | F25 | N/A
| 0 | Record N Over/Undervoltage Duration (high) |  |  | cycles | F3 | N/A
| 0 | Record N Over/Undervoltage Duration (low)
| 0 | Record N Average Voltage (high) |  |  | 0.1  V | F3 | N/A
| 0E3A | Record N Average Voltage (low)
| 0E3B | Reserved
| to |  |  |  |  |  | 
| 0FFF | Reserved
Setpoint Values (Holding Registers) Addresses: 1000 to 131F
METER ID | 1000 | Meter ID characters 1 and 2 | --- | --- | ASCII | F10 | N/A
| 1001 | Meter ID characters 3 and 4 | --- | --- | ASCII | F10 | N/A
| 1002 | Meter ID characters 5 and 6 | --- | --- | ASCII | F10 | N/A
| 1003 | Meter ID characters 7 and 8 | --- | --- | ASCII | F10 | N/A
| 1004 | Meter ID characters 9 and 10 | --- | --- | ASCII | F10 | N/A
| 1005 | Meter ID characters 11 and 12 | --- | --- | ASCII | F10 | N/A
| 1006 | Meter ID characters 13 and 14 | --- | --- | ASCII | F10 | N/A
| 1007 | Meter ID characters 15 and 16 | --- | --- | ASCII | F10 | N/A
| 1008 | Meter ID characters 17 and 18 | --- | --- | ASCII | F10 | N/A
| 1009 | Meter ID characters 19 and 20 | --- | --- | ASCII | F10 | N/A
| 100A | Reserved
| to |  |  |  |  |  | 
| 100F | Reserved
PREFERENCES | 1010 | Default Message Time | 1 to 1201*** | 1 | min x0.1 | F1 | 10 = 1.0 min
| 1011 | Reserved
| 1012 | Display Filter Constant | 1 to 10 | 1 | --- | F1 | 4
| 1013 | Reserved
| to |  |  |  |  |  | 
| 1017 | Reserved
RS485 COM1 SERIAL PORT | 1018 | Serial Communication Address | 1 to 255 | 1 | --- | F1 | 1
| 1019 | Modbus Baud Rate for RS485 COM1 | 0 to 4 | 1 | --- | F12 | 3 = 9600
| 101A | Parity for RS485 COM1 | 0 to 2 | 1 | --- | F13 | 0 = NONE
| 101B | Reserved
| to |  |  |  |  |  | 
| 101F | Reserved
RS485 COM2 SERIAL PORT | 1020 | Modbus Baud Rate for RS485 COM2 | 0 to 4 | 1 | --- | F12 | 3 = 9600
| 1021 | Parity for RS485 COM2 | 0 to 2 | 1 | --- | F13 | 0 = NONE
| 1022 | Reserved
| to |  |  |  |  |  | 
| 1027 | Reserved
RS232 SERIAL PORT | 1028 | Modbus Baud Rate for RS232 | 0 to 4 | 1 | --- | F12 | 3 = 9600
| 1029 | Parity for RS232 | 0 to 2 | 1 | --- | F13 | 0 = NONE
| 102A | Reserved
| to |  |  |  |  |  | 
| 102F | Reserved
CALCU- LATION PARAMETERS | 1030 | Current Demand Calculation Type | 0 to 2 | 1 | --- | F28 | 0 = Thermal Exponential
| 1031 | Current Demand Time Interval | 5 to 180 | 1 | minutes | F1 | 30 min
| 1032 | Power Demand Calculation Type | 0 to 2 | 1 | --- | F28 | 0 = Thermal Exponential
| 1033 | Power Demand Time Interval | 5 to 180 | 1 | minutes | F1 | 30 min
| 1034 | Energy Cost Per kWh | 1 to 50000 | 1 | ¢ x 0.01 | F1 | 10.00 ¢
| 1035 | Extract Fundamental | 0 to 1 | 1 | --- | F11 | 0=DISABLE
| 1036 | Reserved
| 1037 | Reserved
CLEAR DATA | 1038 | Clear Energy Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 1039 | Clear Max Demand Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 103A | Clear Min/Max Current Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 103B | Clear Min/Max Voltage Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 103C | Clear Min/Max Power Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 103D | Clear Max THD Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 103E | Clear Pulse Input Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 103F | Clear Event Record | 0 to 1 | 1 | --- | F31 | 0 = NO
| 1040 | Clear All Demand Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 1041 | Clear Frequency Values | 0 to 1 | 1 | --- | F31 | 0 = NO
| 1042 | Reserved
| 1043 | Reserved
DNP | 1044 | DNP Port | 0 to 3 | 1 | --- | F47 | 0 = NONE
| 1045 | DNP Slave Address | 0 to 255 | 1 | --- | F1 | 0
| 1046 | DNP Turnaround Time | 0 to 100 | 10 | ms | F1 | 10 ms
TARIFF | 1047 | Tariff Period 1 Start Time | 0 to 1439 | 1 | minutes | F1 | 0 min.
| 1048 | Tariff Period 1 Cost per kWh | 1 to 50000 | 1 | ¢  0.01 | F1 | 10.00 ¢
| 1049 | Tariff Period 2 Start Time | 0 to 1439 | 1 | minutes | F1 | 0 min.
| 104A | Tariff Period 2 Cost per kWh | 1 to 50000 | 1 | ¢  0.01 | F1 | 10.00 ¢
| 104B | Tariff Period 3 Start Time | 0 to 1439 | 1 | minutes | F1 | 0 min.
| 104C | Tariff Period 3 Cost per kWh | 1 to 50000 | 1 | ¢  0.01 | F1 | 10.00 ¢
TARIFF continued | 104D | Reserved
| 104E | Reserved
| 104F | Reserved
CURRENT /VOLTAGE CONFIG. | 1050 | Phase CT Primary | 0 to 12000**** | 5 | A | F1 | 0 = OFF
| 1051 | Neutral Current Sensing | 0 to 2 | 1 | --- | F16 | 0 = OFF
| 1052 | Neutral CT Primary | 5 to 6000 | 5 | A | F1 | 100 A
| 1053 | VT Wiring | 0 to 6 | 1 | --- | F15 | 0 = OFF
| 1054 | VT Ratio | 10 to 35000 | 1 | 0.1  ratio | F1 | 1.0:1
| 1055 | VT Nominal Secondary Voltage | 40 to 600 | 1 | V | F1 | 120 V
| 1056 | Nominal Direct Input Voltage | 40 to 600 | 1 | V | F1 | 600 V
| 1057 | Nominal Frequency | 50 to 60 | 10 | Hz | F1 | 60 Hz
| 1058 | CT Wiring | 0 to 3 | 1 | --- | F44 | 0=A,B AND C
| 1059 | Reserved
| to |  |  |  |  |  | 
| 105F | Reserved
ANALOG OUTPUT 1 | 1060 | Analog Output 1 Main Type | 0 to 59 | 1 | --- | F14 | 5=Avg Ph Current
| 1061 | Analog Output 1 Main Min Value | See “Analog Output Parameter Range for Serial Ports” on page COMM-74 |  |  |  | 0
| 1062 | Analog Output 1 Main Max Value | See “Analog Output Parameter Range for Serial Ports” on page COMM-74 |  |  |  | 0
| 1063 | Analog Output 1 Alternate Type | 0 to 59 | 1 | --- | F14 | 0=NOT USED
| 1064 | Analog Output 1 Alternate Min Value | See “Analog Output Parameter Range for Serial Ports” on page COMM-74 |  |  |  | 0
| 1065 | Analog Output 1 Alternate Max Value | See “Analog Output Parameter Range for Serial Ports” on page COMM-74 |  |  |  | 0
| 1066 | Reserved
| 1067 | Analog Output 1 Serial Value |  | 1 | --- | F2 | 0
ANALOG OUTPUT 2 | 1068 | Analog Output 2 Main Type | 0 to 59 | 1 | --- | F14 | 18=3Ph Real Pwr
| 1069 | Analog Output 2 Main Min Value | See “Analog Output Parameter Range for Serial Ports” on page COMM-74 |  |  |  | 0
| 106A | Analog Output 2 Main Max Value | See “Analog Output Parameter Range for Serial Ports” on page COMM-74 |  |  |  | 0
| 106B | Analog Output 2 Alternate Type | 0 to 59 | 1 | --- | F14 | 0=NOT USED
| 106C | Analog Output 2 Alternate Min Value | See “Analog Output Parameter Range for Serial Ports” on page COMM-74 |  |  |  | 0
| 106D | Analog Output 2 Alternate Max Value | See “Analog Output Parameter Range for Serial Ports” on page COMM-74 |  |  |  | 0
| 106E | Reserved
| 106F | Analog Output 2 Serial Value |  | 1 | --- | F2 | 0
ANALOG OUTPUT 3 | 1070 | Analog Output 3 Main Type | 0 to 59 | 1 | --- | F14 | 19=3Ph React Pwr
| 1071 | Analog Output 3 Main Min Value | See “Analog Output Parameter Range for Serial Ports” on page COMM-74
| 1072 | Analog Output 3 Main Max Value | See “Analog Output Parameter Range for Serial Ports” on page COMM-74
| 1073 | Analog Output 3 Alternate Type | 0 to 59 | 1 | --- | F14 | 0=NOT USED
| 1074 | Analog Output 3 Alternate Min Value | See “Analog Output Parameter Range for Serial Ports” on page COMM-74
| 1075 | Analog Output 3 Alternate Max Value | See “Analog Output Parameter Range for Serial Ports” on page COMM-74
| 1076 | Reserved
| 1077 | Analog Output 3 Serial Value |  | 1 | --- | F2 | 0
ANALOG OUTPUT 4 | 1078 | Analog Output 4 Main Type | 0 to 59 | 1 | --- | F14 | 17=3Ph Pwr Factor
| 1079 | Analog Output 4 Main Min Value | See “Analog Output Parameter Range for Serial Ports” on page COMM-74
| 107A | Analog Output 4 Main Max Value | See “Analog Output Parameter Range for Serial Ports” on page COMM-74
| 107B | Analog Output 4 Alternate Type | 0 to 59 | 1 | --- | F14 | 0=NOT USED
| 107C | Analog Output 4 Alternate Min Value | See “Analog Output Parameter Range for Serial Ports” on page COMM-74
| 107D | Analog Output 4 Alternate Max Value | See “Analog Output Parameter Range for Serial Ports” on page COMM-74
| 107E | Reserved
| 107F | Analog Output 4 Serial Value |  | 1 | --- | F2 | 0
ANALOG INPUT | 1080 | Analog Input Main/Alt Select Relay | 0 to 3 | 1 | --- | F19 | 0=OFF
| 1081 | Analog In Main Name 1st and 2nd char. | --- | --- | ASCII | F10 | ““
| 1082 | Analog In Main Name 3rd and 4th char. | --- | --- | ASCII | F10 | “MA”
| 1083 | Analog In Main Name 5th and 6th char. | --- | --- | ASCII | F10 | “IN”
| 1084 | Analog In Main Name 7th and 8th char. | --- | --- | ASCII | F10 | “ A”
| 1085 | Analog In Main Name 9th and 10th char. | -- | -- | ASCII | F10 | “NA”
| 1086 | Analog In Main Name 11th and 12th char. | -- | -- | ASCII | F10 | “LO”
| 1087 | Analog In Main Name 13th and 14th char. | --- | --- | ASCII | F10 | “G “
| 1088 | Analog In Main Name 15h and 16th char. | ---- | ---- | ASCII | F10 | “IN”
| 1089 | Analog In Main Name 17th and 18th char. | --- | --- | ASCII | F10 | “PU”
| 108A | Analog In Main Name 19th and 20th char. | --- | --- | ASCII | F10 | “T “
| 108B | Analog In Main Units 1st and 2nd char. | --- | --- | ASCII | F10 | “ U”
| 108C | Analog In Main Units 3rd and 4th char. | --- | --- | ASCII | F10 | “ni”
| 108D | Analog In Main Units 5th and 6th char. | --- | --- | ASCII | F10 | “ts”
| 108E | Analog In Main Units 7th and 8th char. | --- | --- | ASCII | F10 | “”
| 108F | Analog In Main Units 9th and 10th char. | --- | --- | ASCII | F10 | ““
| 1090 | Analog Input Main 4 mA Value | 0 to 65000 | 1 | --- | F1 | 0
| 1091 | Analog Input Main 20 mA Value | 0 to 65000 | 1 | --- | F1 | 0
| 1092 | Analog Input Main Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1093 | Analog Input Main Level | 0 to 65000 | 1 | --- | F1 | 0
| 1094 | Analog Input Main Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1095 | Reserved
| 1096 | Reserved
| 1097 | Reserved
| 1098 | Analog In Alt Name 1st and 2nd char. | --- | --- | ASCII | F10 | ““
| 1099 | Analog In Alt Name 3rd and 4th char. | --- | --- | ASCII | F10 | “AL”
| 109A | Analog In Alt Name 5th and 6th char. | --- | --- | ASCII | F10 | “T ”
| 109B | Analog In Alt Name 7th and 8th char. | --- | --- | ASCII | F10 | “ A”
| 109C | Analog In Alt Name 9th and 10th char. | -- | -- | ASCII | F10 | “NA”
| 109D | Analog In Alt Name 11th and 12th char. | -- | -- | ASCII | F10 | “LO”
| 109E | Analog In Alt Name 13th and 14th char. | --- | --- | ASCII | F10 | “G ”
| 109F | Analog In Alt Name 15h and 16th char. | ---- | ---- | ASCII | F10 | “IN”
| 10A0 | Analog In Alt Name 17th and 18th char. | --- | --- | ASCII | F10 | “PU”
ANALOG INPUT continued | 10A1 | Analog In Alt Name 19th and 20th char. | --- | --- | ASCII | F10 | “T “
| 10A2 | Analog In Alt Units 1st and 2nd char. | --- | --- | ASCII | F10 | “ U”
| 10A3 | Analog In Alt Units 3rd and 4th char. | --- | --- | ASCII | F10 | “ni”
| 10A4 | Analog In Alt Units 5th and 6th char. | --- | --- | ASCII | F10 | “ts”
| 10A5 | Analog In Alt Units 7th and 8th char. | --- | --- | ASCII | F10 | “ ”
| 10A6 | Analog In Alt Units 9th and 10th char. | --- | --- | ASCII | F10 | “ ”
| 10A7 | Analog Input Alt 4 mA Value | 0 to 65000 | 1 | --- | F1 | 0
| 10A8 | Analog Input Alt 20 mA Value | 0 to 65000 | 1 | --- | F1 | 0
| 10A9 | Analog Input Alt Relay | 0-4 | 1 | --- | F29 | 0=OFF
| 10AA | Analog Input Alt Level | 0 to 65000 | 1 | --- | F1 | 0
| 10AB | Analog Input Alt Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 10AC | Reserved
| to |  |  |  |  |  | 
| 10AF | Reserved
SWITCH A | 10B0 | Switch A Name characters 1 and 2 | --- | --- | ASCII | F10 | “ ”
| 10B1 | Switch A Name characters 3 and 4 | --- | --- | ASCII | F10 | “ S”
| 10B2 | Switch A Name characters 5 and 6 | --- | --- | ASCII | F10 | “WI”
| 10B3 | Switch A Name characters 7 and 8 | --- | --- | ASCII | F10 | “TC”
| 10B4 | Switch A Name characters 9 and 10 | --- | --- | ASCII | F10 | “H ”
| 10B5 | Switch A Name characters 11 and 12 | --- | --- | ASCII | F10 | “IN“
| 10B6 | Switch A Name characters 13 and 14 | --- | --- | ASCII | F10 | “PU”
| 10B7 | Switch A Name characters 15 and 16 | --- | --- | ASCII | F10 | “T ”
| 10B8 | Switch A Name characters 17 and 18 | --- | --- | ASCII | F10 | “A ”
| 10B9 | Switch A Name characters 19 and 20 | --- | --- | ASCII | F10 | “ ”
| 10BA | Switch A Function | 0 to 14 | 1 | --- | F20 | 0 = Not Used
| 10BB | Switch A Activation | 0 to 1 | 1 | --- | F27 | 1 = Closed
| 10BC | Switch A Time Delay | 0 to 6000 | 1 | 0.1 x s | F1 | 0.0 s
| 10BD | Reserved
| 10BE | Reserved
| 10BF | Reserved
SWITCH B | 10C0 | Switch B Name characters 1 and 2 | --- | --- | ASCII | F10 | “ ”
| 10C1 | Switch B Name characters 3 and 4 | --- | --- | ASCII | F10 | “ S”
| 10C2 | Switch B Name characters 5 and 6 | --- | --- | ASCII | F10 | “WI”
| 10C3 | Switch B Name characters 7 and 8 | --- | --- | ASCII | F10 | “TC”
| 10C4 | Switch B Name characters 9 and 10 | --- | --- | ASCII | F10 | “H ”
| 10C5 | Switch B Name characters 11 and 12 | --- | --- | ASCII | F10 | “IN“
| 10C6 | Switch B Name characters 13 and 14 | --- | --- | ASCII | F10 | “PU”
| 10C7 | Switch B Name characters 15 and 16 | --- | --- | ASCII | F10 | “T ”
| 10C8 | Switch B Name characters 17 and 18 | --- | --- | ASCII | F10 | “B ”
| 10C9 | Switch B Name characters 19 and 20 | --- | --- | ASCII | F10 | “ ”
| 10CA | Switch B Function | 0 to 14 | 1 | --- | F20 | 0=NOT USED
| 10CB | Switch B Activation | 0 to 1 | 1 | --- | F27 | 1=CLOSED
| 10CC | Switch B Time Delay | 0 to 6000 | 1 | 0.1 x s | F1 | 0.0 s
| 10CD | Reserved
| 10CE | Reserved
| 10CF | Reserved
SWITCH C | 10D0 | Switch C Name characters 1 and 2 | --- | --- | ASCII | F10 | “ ”
| 10D1 | Switch C Name characters 3 and 4 | --- | --- | ASCII | F10 | “ S”
| 10D2 | Switch C Name characters 5 and 6 | --- | --- | ASCII | F10 | “WI”
| 10D3 | Switch C Name characters 7 and 8 | --- | --- | ASCII | F10 | “TC”
| 10D4 | Switch C Name characters 9 and 10 | --- | --- | ASCII | F10 | “H ”
| 10D5 | Switch C Name characters 11 and 12 | --- | --- | ASCII | F10 | “IN”
| 10D6 | Switch C Name characters 13 and 14 | --- | --- | ASCII | F10 | “PU”
| 10D7 | Switch C Name characters 15 and 16 | --- | --- | ASCII | F10 | “T ”
| 10D8 | Switch C Name characters 17 and 18 | --- | --- | ASCII | F10 | “C ”
| 10D9 | Switch C Name characters 19 and 20 | --- | --- | ASCII | F10 | “ ”
| 10DA | Switch C Function | 0 to 14 | 1 | --- | F20 | 0=NOT USED
| 10DB | Switch C Activation | 0 to 1 | 1 | --- | F27 | 1=CLOSED
| 10DC | Switch C Time Delay | 0 to 6000 | 1 | 0.1 x s | F1 | 0.0 s
| 10DD | Reserved
| 10DE | Reserved
| 10DF | Reserved
SWITCH D | 10E0 | Switch D Name characters 1 and 2 | --- | --- | ASCII | F10 | “ ”
| 10E1 | Switch D Name characters 3 and 4 | --- | --- | ASCII | F10 | “ S”
| 10E2 | Switch D Name characters 5 and 6 | --- | --- | ASCII | F10 | “WI”
| 10E3 | Switch D Name characters 7 and 8 | --- | --- | ASCII | F10 | “TC”
| 10E4 | Switch D Name characters 9 and 10 | --- | --- | ASCII | F10 | “H ”
| 10E5 | Switch D Name characters 11 and 12 | --- | --- | ASCII | F10 | “IN”
| 10E6 | Switch D Name characters 13 and 14 | --- | --- | ASCII | F10 | “PU”
| 10E7 | Switch D Name characters 15 and 16 | --- | --- | ASCII | F10 | “T ”
| 10E8 | Switch D Name characters 17 and 18 | --- | --- | ASCII | F10 | “D ”
| 10E9 | Switch D Name characters 19 and 20 | --- | --- | ASCII | F10 | “ ”
| 10EA | Switch D Function | 0 to 14 | 1 | --- | F20 | 0=NOT USED
| 10EB | Switch D Activation | 0 to 1 | 1 | --- | F27 | 1=CLOSED
| 10EC | Switch D Time Delay | 0 to 6000 | 1 | 0.1 x s | F1 | 0.0 s
| 10ED | Reserved
| 10EE | Reserved
| 10EF | Reserved
PULSE OUTPUT | 10F0 | Positive kWh Pulse Output Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 10F1 | Positive kWh Pulse Output Interval | 1 to 65000 | 1 | kWh | F1 | 100 kWh
| 10F2 | Negative kWh Pulse Output Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 10F3 | Negative kWh Pulse Output Interval | 1 to 65000 | 1 | kWh | F1 | 100 kWh
| 10F4 | Positive kvarh Pulse Output Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 10F5 | Positive kvarh Pulse Output Interval | 1 to 65000 | 1 | kvarh | F1 | 100 kvarh
| 10F6 | Negative kvarh Pulse Output Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 10F7 | Negative kvarh Pulse Output Interval | 1 to 65000 | 1 | kvarh | F1 | 100 kvarh
| 10F8 | kVAh Pulse Output Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 10F9 | kVAh Pulse Output Interval | 1 to 65000 | 1 | kVAh | F1 | 100 kVAh
| 10FA | Pulse Output Width | 100 to 2000 | 10 | ms | F1 | 100 ms
| 10FB | Serial Pulse Relay Interval | 100 to 10000 | 100 | ms | F1 | 100 ms
| 10FC | Reserved
PULSE INPUT | 10FD | Pulse Input Units 1st and 2nd char. | --- | --- | ASCII | F10 | “ U”
| 10FE | Pulse Input Units 3rd and 4th char. | --- | --- | ASCII | F10 | “ni”
| 10FF | Pulse Input Units 5th and 6th char. | --- | --- | ASCII | F10 | “ts”
| 1100 | Pulse Input Units 7th and 8th char. | --- | --- | ASCII | F10 | “ ”
| 1101 | Pulse Input Units 9th and 10th char. | --- | --- | ASCII | F10 | “ ”
| 1102 | Pulse Input 1 Value | 0 to 65000 | 1 | Units | F1 | 1
| 1103 | Pulse Input 2 Value | 0 to 65000 | 1 | Units | F1 | 1
| 1104 | Pulse Input 3 Value | 0 to 65000 | 1 | Units | F1 | 1
| 1105 | Pulse Input 4 Value | 0 to 65000 | 1 | Units | F1 | 1
| 1106 | Pulse Input Total | 0 to 10 | 1 | --- | F43 | 9 = 1+2+3+4
| 1107 | Reserved
ALARM RELAY | 1108 | Alarm Relay Operation | 0 to 1 | 1 | --- | F17 | 0 = NON-FAILSAFE
| 1109 | Alarm Relay Activation | 0 to 1 | 1 | --- | F18 | 0 = UNLATCHED
| 110A | Reserved
| to |  |  |  |  |  | 
| 110F | Reserved
AUXILIARY RELAY 1 | 1110 | Auxiliary Relay 1 Operation | 0 to 1 | 1 | --- | F17 | 0 = NON-FAILSAFE
| 1111 | Auxiliary Relay 1 Activation | 0 to 1 | 1 | --- | F18 | 0 = UNLATCHED
| 1112 | Reserved
| to |  |  |  |  |  | 
| 1117 | Reserved
AUXILIARY RELAY 2 | 1118 | Auxiliary Relay 2 Operation | 0 to 1 | 1 | --- | F17 | 0 = NON-FAILSAFE
| 1119 | Auxiliary Relay 2 Activation | 0 to 1 | 1 | --- | F18 | 0 = UNLATCHED
| 111A | Reserved
| to |  |  |  |  |  | 
| 111F | Reserved
AUXILIARY RELAY 3 | 1120 | Auxiliary Relay 3 Operation | 0 to 1 | 1 | --- | F17 | 0 = NON-FAILSAFE
| 1121 | Auxiliary Relay 3 Activation | 0 to 1 | 1 | --- | F18 | 0 = UNLATCHED
| 1122 | Reserved
| 1123 | Reserved
| 1124 | Reserved
| 1125 | Reserved
CURRENT/ VOLTAGE ALARMS | 1126 | Phase Overcurrent Activation | 0 to 1 | 1 | --- | F115 | 0=AVERAGE
| 1127 | Detect I/V Alarms Using Percentage | 0 to 1 | 1 | --- | F31 | 0=NO
| 1128 | Phase Undercurrent Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1129 | Phase Undercurrent Level in Amps | 1 to 12000 | 1 | A | F1 | 100 A
| 112A | Phase Undercurrent Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 112B | Phase Overcurrent Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 112C | Phase Overcurrent Level in Amps | 1 to 12000 | 1 | A | F1 | 100 A
| 112D | Phase Overcurrent Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 112E | Neutral Overcurrent Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 112F | Neutral Overcurrent Level in Amps | 1 to 12000 | 1 | A | F1 | 100 A
| 1130 | Neutral Overcurrent Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1131 | Undervoltage Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1132 | Undervoltage Level in Volts | 20 to 65000 | 1 | V | F1 | 100 V
| 1133 | Undervoltage Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
CURRENT/ VOLTAGE ALARMS continued | 1134 | Phases Req’d for Operation of Undervoltage | 0 to 2 | 1 | --- | F30 | 0=ANY ONE
| 1135 | Detect Undervoltage Below 20 V | 0 to 1 | 1 | --- | F11 | 0=DISABLE
| 1136 | Overvoltage Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1137 | Overvoltage Level in Volts | 1 to 65000 | 1 | V | F1 | 100 V
| 1138 | Overvoltage Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1139 | Phases Req’d for Operation of Overvoltage | 0 to 2 | 1 | --- | F30 | 0=ANY ONE
| 113A | Phase Current Unbalance Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 113B | Phase Current Unbalance Level | 1 to 100 | 1 | % | F1 | 10%
| 113C | Phase Current Unbalance Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 113D | Voltage Unbalance Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 113E | Voltage Unbalance Level | 1 to 100 | 1 | % | F1 | 10%
| 113F | Voltage Unbalance Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1140 | Voltage Phase Reversal Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1141 | Voltage Phase Reversal Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1142 | Detect Undercurrent When 0A | 0 to 1 | 1 | --- | F31 | 0=NO
| 1143 | Phase Undercurrent Level in % of CT | 1 to 100 | 1 | % | F1 | 100%
| 1144 | Phase Overcurrent Level in % of CT | 1 to 150 | 1 | % | F1 | 100%
| 1145 | Neutral Overcurrent Level in % of CT | 1 to 150 | 1 | % | F1 | 100%
| 1146 | Undervoltage Level in % of VT | 20 to 100 | 1 | % | F1 | 100%
| 1147 | Overvoltage Level in % of VT | 20 to 150 | 1 | % | F1 | 100%
TOTAL HARMONIC DISTORTION ALARMS | 1148 | Average Current THD Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1149 | Average Current THD Level | 5 to 1000 | 5 | 0.1 x % | F1 | 100=10.0%
| 114A | Average Current THD Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 114B | Average Voltage THD Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 114C | Average Voltage THD Level | 5 to 1000 | 5 | 0.1 x % | F1 | 100=10.0%
| 114D | Average Voltage THD Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 114E | Reserved
| to |  |  |  |  |  | 
| 1157 | Reserved
FREQUENCY ALARMS | 1158 | Underfrequency Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1159 | Underfrequency Level | 2000 to 7000 | 1 | 0.01 x Hz | F1 | 40.00 Hz
| 115A | Underfrequency Delay | 1 to 100 | 1 | 0.1 x s | F1 | 100=10.0 s
| 115B | Zero Frequency Detect | 0 to 1 | 1 | --- | F11 | 0=DISABLE
| 115C | Overfrequency Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 115D | Overfrequency Level | 2000 to 12500 | 1 | 0.01 x Hz | F1 | 70.00 Hz
| 115E | Overfrequency Delay | 1 to 100 | 1 | 0.1 x s | F1 | 100=10.0 s
| 115F | Reserved
| to |  |  |  |  |  | 
| 1166 | Reserved
POWER ALARMS | 1167 | Power Alarms Level Base Units | 0 to 1 | 1 | --- | F114 | 0=kW/kVAR
| 1168 | Positive Real Power Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1169 | Positive Real Power Level in kW | 1 to 65000 | 1 | kW | F1 | 1000 kW
| 116A | Positive Real Power Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 116B | Negative Real Power Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 116C | Negative Real Power Level in kW | 1 to 65000 | 1 | kW | F1 | 1000 kW
POWER ALARMS continued | 116D | Negative Real Power Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 116E | Positive Reactive Power Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 116F | Positive Reactive Power Level in kVAR | 1 to 65000 | 1 | kVAR | F1 | 1000 kVAR
| 1170 | Positive Reactive Power Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1171 | Negative Reactive Power Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1172 | Negative Reactive Power Level in kVAR | 1 to 65000 | 1 | kVAR | F1 | 1000 kVAR
| 1173 | Negative Reactive Power Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1174 | Positive Real Power Level in MW | 1 to 65000 | 1 | 0.01 MW | F1 | 10.00MW
| 1175 | Negative Real Power Level in MW | 1 to 65000 | 1 | 0.01 MW | F1 | 10.00MW
| 1176 | Positive Reactive Power Level in MVAR | 1 to 65000 | 1 | 0.01 MVAR | F1 | 10.00MVAR
| 1177 | Negative Reactive Power Level in MVAR | 1 to 65000 | 1 | 0.01 MVAR | F1 | 10.00MVAR
POWER FACTOR ALARMS | 1178 | Power Factor Lead 1 Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1179 | Power Factor Lead 1 Pickup Level | 0 to 100 | 1 | 0.01 x PF | F1 | 0.99
| 117A | Power Factor Lead 1 Dropout Level | 0 to 100 | 1 | 0.01 x PF | F1 | 1
| 117B | Power Factor Lead 1 Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 117C | Power Factor Lag 1 Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 117D | Power Factor Lag 1 Pickup Level | 0 to 100 | 1 | 0.01 x PF | F1 | 0.99
| 117E | Power Factor Lag 1 Dropout Level | 0 to 100 | 1 | 0.01 x PF | F1 | 1
| 117F | Power Factor Lag 1 Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1180 | Power Factor Lead 2 Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1181 | Power Factor Lead 2 Pickup Level | 0 to 100 | 1 | 0.01 x PF | F1 | 0.99
| 1182 | Power Factor Lead 2 Dropout Level | 0 to 100 | 1 | 0.01 x PF | F1 | 1
| 1183 | Power Factor Lead 2 Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1184 | Power Factor Lag 2 Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1185 | Power Factor Lag 2 Pickup Level | 0 to 100 | 1 | 0.01 x PF | F1 | 0.99
| 1186 | Power Factor Lag 2 Dropout Level | 0 to 100 | 1 | 0.01 x PF | F1 | 1
| 1187 | Power Factor Lag 2 Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 1188 | Reserved
| to |  |  |  |  |  | 
| 118F | Reserved
DEMAND ALARMS | 1190 | Phase A Current Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1191 | Phase A Current Demand Level | 10 to 7500 | 1 | A | F1 | 100 A
| 1192 | Phase B Current Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1193 | Phase B Current Demand Level | 10 to 7500 | 1 | A | F1 | 100 A
| 1194 | Phase C Current Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1195 | Phase C Current Demand Level | 10 to 7500 | 1 | A | F1 | 100 A
| 1196 | Neutral Current Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1197 | Neutral Current Demand Level | 10 to 7500 | 1 | A | F1 | 100 A
| 1198 | Positive Real Power Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 1199 | Positive Real Power Demand Level | 1 to 65000 | 1 | kW | F1 | 1000 kW
| 119A | Positive Reactive Power Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 119B | Positive Reactive Power Demand Level | 1 to 65000 | 1 | kvar | F1 | 1000 kvar
| 119C | Apparent Power Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 119D | Apparent Power Demand Level | 1 to 65000 | 1 | kVA | F1 | 1000 kVA
| 119E | Negative Real Power Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 119F | Negative Real Power Demand Level | 1 to 65000 | 1 | kW | F1 | 1000 kW
DEMAND ALARMS continued | 11A0 | Negative Reactive Power Demand Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 11A1 | Negative Reactive Power Demand Level | 1 to 65000 | 1 | kvar | F1 | 1000 kvar
| 11A2 | Reserved
| to |  |  |  |  |  | 
| 11A7 | Reserved
PULSE INPUT ALARMS | 11A8 | Pulse Input 1 Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 11A9 | Pulse Input 1 Level | 1 to 65000 | 1 | --- | F1 | 100
| 11AA | Pulse Input 1 Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 11AB | Reserved
| to |  |  |  |  |  | 
| 11AF | Reserved
MISC. ALARMS | 11B0 | Serial COM1 Failure Alarm Delay | 5 to 61*** | 1 | s | F1 | 61=OFF
| 11B1 | Serial COM2 Failure Alarm Delay | 5 to 61*** | 1 | s | F1 | 61=OFF
| 11B2 | Clock Not Set Alarm | 0 to 1 | 1 | --- | F11 | 0 = DISABLED
| 11B3 | Data Log 1 Percentage Full Alarm Level | 50 to 101*** | 1 | % | F1 | 101=OFF
| 11B4 | Data Log 2 Percentage Full Alarm Level | 50 to 101*** | 1 | % | F1 | 101=OFF
| 11B5 | Reserved
| 11B6 | Reserved
| 11B7 | Reserved
PULSE INPUT ALARMS | 11B8 | Pulse Input 2 Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 11B9 | Pulse Input 2 Level | 1 to 65000 | 1 | --- | F1 | 100
| 11BA | Pulse Input 2 Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 11BB | Pulse Input 3 Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 11BC | Pulse Input 3 Level | 1 to 65000 | 1 | --- | F1 | 100
| 11BD | Pulse Input 3 Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 11BE | Pulse Input 4 Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 11BF | Pulse Input 4 Level | 1 to 65000 | 1 | --- | F1 | 100
| 11C0 | Pulse Input 4 Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 11C1 | Totalized Pulse Input Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 11C2 | Totalized Pulse Input Level | 1 to 65000 | 1 | --- | F1 | 100
| 11C3 | Totalized Pulse Input Delay | 5 to 6000 | 5 | 0.1 x s | F1 | 100=10.0 s
| 11C4 | Reserved
| to |  |  |  |  |  | 
| 11C7 | Reserved
SIMULATION | 11C8 | Current/Voltage Simulation | 0 to 1 | 1 | --- | F11 | 0=OFF
| 11C9 | Current/Voltage Simulation Time | 5 to 305 | 5 | min | F1***** | 15 min
| 11CA | Phase A Current | 0 to 10000 | 1 | A | F1 | 0 A
| 11CB | Phase B Current | 0 to 10000 | 1 | A | F1 | 0 A
| 11CC | Phase C Current | 0 to 10000 | 1 | A | F1 | 0 A
| 11CD | Neutral Current | 0 to 10000 | 1 | A | F1 | 0 A
| 11CE | Vax Voltage | 0 to 65000 | 1 | V | F1 | 0 V
| 11CF | Vbx Voltage | 0 to 65000 | 1 | V | F1 | 0 V
| 11D0 | Vcx Voltage | 0 to 65000 | 1 | V | F1 | 0 V
| 11D1 | Phase Angle | 0 to 359 | 1 | degrees | F1 | 0 degrees
SIMULATION continued | 11D2 | Analog Output Simulation | 0 to 1 | 1 | --- | F11 | 0=OFF
| 11D3 | Analog Output Simulation Time | 5 to 305 | 5 | min | F1***** | 15 min
| 11D4 | Analog Output 1 | 0 to 1201*** | 1 | 0.1 x % | F1 | 1201=OFF
| 11D5 | Analog Output 2 | 0 to 1201*** | 1 | 0.1 x % | F1 | 1201=OFF
| 11D6 | Analog Output 3 | 0 to 1201*** | 1 | 0.1 x % | F1 | 1201=OFF
| 11D7 | Analog Output 4 | 0 to 1201*** | 1 | 0.1 x % | F1 | 1201=OFF
| 11D8 | Analog Input Simulation | 0 to 1 | 1 | --- | F11 | 0=OFF
| 11D9 | Analog Input Simulation Time | 5 to 305 | 5 | min | F1***** | 15 min
| 11DA | Analog Input | 40 to 201 | 1 | 0.1 x mA | F1 | 201=OFF
| 11DB | Switch Input Simulation | 0 to 1 | 1 | --- | F11 | 0=OFF
| 11DC | Switch Input Simulation Time | 5 to 305 | 5 | min | F1***** | 15 min
| 11DD | Switch Input A | 0 to 1 | 1 | --- | F27 | 0=OPEN
| 11DE | Switch Input B | 0 to 1 | 1 | --- | F27 | 0=OPEN
| 11DF | Switch Input C | 0 to 1 | 1 | --- | F27 | 0=OPEN
| 11E0 | Switch Input D | 0 to 1 | 1 | --- | F27 | 0=OPEN
| 11E1 | Reserved
| 11E2 | Reserved
| 11E3 | Reserved
TIME ALARM | 11E4 | Time Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 11E5 | Pickup Time Hours/Minutes | 0 to 65535 | 1 | hr./min | F22 | 12:00
| 11E6 | Pickup Time Seconds | 0 to 59000 | 1000 | ms | F1 | 0
| 11E7 | Dropout Time Hours/Minutes | 0 to 65535 | 1 | hr./min | F22 | 12:00
| 11E8 | Dropout Time Seconds | 0 to 59000 | 1000 | ms | F1 | 0
| 11E9 | Reserved
| to |  |  |  |  |  | 
| 11EF | Reserved
PROGRAM- MABLE MESSAGE | 11F0 | Programmable message chars 1 & 2 | 32 to 127 | 1 | ASCII | F10 | “Ph”
| 11F1 | Programmable message chars 3 & 4 | 32 to 127 | 1 | ASCII | F10 | “on”
| 11F2 | Programmable message chars 5 & 6 | 32 to 127 | 1 | ASCII | F10 | “e:”
| 11F3 | Programmable message chars 7 & 8 | 32 to 127 | 1 | ASCII | F10 | “ 9”
| 11F4 | Programmable message chars 9 & 10 | 32 to 127 | 1 | ASCII | F10 | “05”
| 11F5 | Programmable message chars 11 & 12 | 32 to 127 | 1 | ASCII | F10 | “-2”
| 11F6 | Programmable message chars 13 & 14 | 32 to 127 | 1 | ASCII | F10 | “94”
| 11F7 | Programmable message chars 15 & 16 | 32 to 127 | 1 | ASCII | F10 | “-6”
| 11F8 | Programmable message chars 17 & 18 | 32 to 127 | 1 | ASCII | F10 | “22”
| 11F9 | Programmable message chars 19 & 20 | 32 to 127 | 1 | ASCII | F10 | “2 ”
| 11FA | Programmable message chars 21 & 22 | 32 to 127 | 1 | ASCII | F10 | “GE”
| 11FB | Programmable message chars 23 & 24 | 32 to 127 | 1 | ASCII | F10 | “in”
| 11FC | Programmable message chars 25 & 26 | 32 to 127 | 1 | ASCII | F10 | “du”
| 11FD | Programmable message chars 27 & 28 | 32 to 127 | 1 | ASCII | F10 | “st”
| 11FE | Programmable message chars 29 & 30 | 32 to 127 | 1 | ASCII | F10 | “ri”
| 11FF | Programmable message chars 31 & 32 | 32 to 127 | 1 | ASCII | F10 | “al”
| 1200 | Programmable message chars 33 & 34 | 32 to 127 | 1 | ASCII | F10 | “.c”
| 1201 | Programmable message chars 35 & 36 | 32 to 127 | 1 | ASCII | F10 | “om”
| 1202 | Programmable message chars 37 & 38 | 32 to 127 | 1 | ASCII | F10 | “/p”
| 1203 | Programmable message chars 39 & 40 | 32 to 127 | 1 | ASCII | F10 | “m ”
PROGRAM- MABLE MESSAGE continued | 1204 | Reserved
| to |  |  |  |  |  | 
| 120F | Reserved
FLASH MESSAGE | 1210 | Flash message characters 1 and 2 | 32 to 127 | 1 | ASCII | F10 | “”
| 1211 | Flash message characters 3 and 4 | 32 to 127 | 1 | ASCII | F10 | “”
| 1212 | Flash message characters 5 and 6 | 32 to 127 | 1 | ASCII | F10 | “”
| 1213 | Flash message characters 7 and 8 | 32 to 127 | 1 | ASCII | F10 | “”
| 1214 | Flash message characters 9 and 10 | 32 to 127 | 1 | ASCII | F10 | “”
| 1215 | Flash message characters 11 and 12 | 32 to 127 | 1 | ASCII | F10 | “”
| 1216 | Flash message characters 13 and 14 | 32 to 127 | 1 | ASCII | F10 | “”
| 1217 | Flash message characters 15 and 16 | 32 to 127 | 1 | ASCII | F10 | “”
| 1218 | Flash message characters 17 and 18 | 32 to 127 | 1 | ASCII | F10 | “”
| 1219 | Flash message characters 19 and 20 | 32 to 127 | 1 | ASCII | F10 | “”
| 121A | Flash message characters 21 and 22 | 32 to 127 | 1 | ASCII | F10 | “”
| 121B | Flash message characters 23 and 24 | 32 to 127 | 1 | ASCII | F10 | “”
| 121C | Flash message characters 25 and 26 | 32 to 127 | 1 | ASCII | F10 | “”
| 121D | Flash message characters 27 and 28 | 32 to 127 | 1 | ASCII | F10 | “”
| 121E | Flash message characters 29 and 30 | 32 to 127 | 1 | ASCII | F10 | “”
| 121F | Flash message characters 31 and 32 | 32 to 127 | 1 | ASCII | F10 | “”
| 1220 | Flash message characters 33 and 34 | 32 to 127 | 1 | ASCII | F10 | “”
| 1221 | Flash message characters 35 and 36 | 32 to 127 | 1 | ASCII | F10 | “”
| 1222 | Flash message characters 37 and 38 | 32 to 127 | 1 | ASCII | F10 | “”
| 1223 | Flash message characters 39 and 40 | 32 to 127 | 1 | ASCII | F10 | “”
| 1224 | Reserved
| to |  |  |  |  |  | 
| 125F | Reserved
DATA LOGGER | 1260 | Log 1 Interval (high) | 1 to 86400 | 1 | s | F3 | 3600
| 1261 | Log 1 Interval (low)
| 1262 | Log 2 Interval (high) | 1 to 86400 | 1 | s | F3 | 3600
| 1263 | Log 2 Interval (low)
| 1264 | Log 1 Mode | 0 to 1 | 1 | --- | F32 | 0 = RUN TO FILL
| 1265 | Log 2 Mode | 0 to 1 | 1 | --- | F32 | 0 = RUN TO FILL
| 1266 | Log Size Determination | 0 to 1 | 1 | --- | F33 | 0 = AUTOMATIC
| 1267 | Log 1 Size | 0 to 100 | 1 | % | F1 | 50%
| 1268 | Data Log Memory Access Block Number | 0 to 511 | 1 | --- | F1 | 0
| 1269 | Stop Data Log 1 | 0 to 1 | 1 | --- | F31 | 0=NO
| 126A | Stop Data Log 2 | 0 to 1 | 1 | --- | F31 | 0=NO
| 126B | Reserved
| to |  |  |  |  |  | 
| 126F | Reserved
| 1270 | Ia Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1271 | Ib Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1272 | Ic Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1273 | Iavg Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1274 | In Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1275 | I Unbalance Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
DATA LOGGER continued | 1276 | Van Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1277 | Vbn Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1278 | Vcn Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1279 | Vp avg Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 127A | Vab Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 127B | Vbc Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 127C | Vca Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 127D | Vl avg Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 127E | V Unbalance Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 127F | Pa Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1280 | Qa Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1281 | Sa Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1282 | PFa Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1283 | Pb Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1284 | Qb Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1285 | Sb Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1286 | PFb Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1287 | Pc Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1288 | Qc Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1289 | Sc Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 128A | PFc Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 128B | P3 Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 128C | Q3 Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 128D | S3 Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 128E | PF3 Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 128F | Frequency Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1290 | Positive kWh Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1291 | Negative kWh Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1292 | Positive kvarh Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1293 | Negative kvarh Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1294 | kVAh Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1295 | Ia Demand Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1296 | Ib Demand Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1297 | Ic Demand Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1298 | In Demand Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 1299 | P3 Demand Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 129A | Q3 Demand Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 129B | S3 Demand Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 129C | Ia THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 129D | Ib THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 129E | Ic THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 129F | In THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 12A0 | Van THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 12A1 | Vbn THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 12A2 | Vcn THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 12A3 | Vab THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
DATA LOGGER continued | 12A4 | Vbc THD Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 12A5 | Analog Input Log Assignment | 0 to 3 | 1 | --- | F34 | 0 = NONE
| 12A6 | Reserved
| to |  |  |  |  |  | 
| 12BF | Reserved
EVENT RECORDER | 12C0 | Event Recorder Memory Access Event Num | 0 to 65535 | 1 | --- | F1 | 0
| 12C1 | Event Recorder Operation | 0 to 1 | 1 | --- | F11 | 0 = DISABLE
| 12C2 | Event Recorder Event Enable Flags 1 | 0 to 65535 | 1 | --- | F105 | 65535
| 12C3 | Event Recorder Event Enable Flags 2 | 0 to 65535 | 1 | --- | F106 | 65535
| 12C4 | Event Recorder Event Enable Flags 3 | 0 to 65535 | 1 | --- | F107 | 65535
| 12C5 | Event Recorder Event Enable Flags 4 | 0 to 65535 | 1 | --- | F112 | 65535
| 12C6 | Reserved
| to |  |  |  |  |  | 
| 12CF | Reserved
TRACE MEMORY | 12D0 | Trace Memory Usage | 0 to 2 | 1 | --- | F37 | 0=1x36 cycles
| 12D1 | Trace Memory Trigger Mode | 0 to 1 | 1 | --- | F38 | 0=ONE SHOT
| 12D2 | Ia Overcurrent Trigger Level | 1 to 151*** | 1 | % CT | F1 | 151=OFF
| 12D3 | Ib Overcurrent Trigger Level | 1 to 151*** | 1 | % CT | F1 | 151=OFF
| 12D4 | Ic Overcurrent Trigger Level | 1 to 151*** | 1 | % CT | F1 | 151=OFF
| 12D5 | In Overcurrent Trigger Level | 1 to 151*** |  | % CT | F1 | 151=OFF
| 12D6 | Va Overvoltage Trigger Level | 20 to 151*** | 1 | % VT | F1 | 151=OFF
| 12D7 | Vb Overvoltage Trigger Level | 20 to 151*** | 1 | % VT | F1 | 151=OFF
| 12D8 | Vc Overvoltage Trigger Level | 20 to 151*** | 1 | % VT | F1 | 151=OFF
| 12D9 | Va Undervoltage Trigger Level | 20 to 151*** | 1 | % VT | F1 | 151=OFF
| 12DA | Vb Undervoltage Trigger Level | 20 to 151*** | 1 | % VT | F1 | 151=OFF
| 12DB | Vc Undervoltage Trigger Level | 20 to 151*** | 1 | % VT | F1 | 151=OFF
| 12DC | Switch Input A Trigger | 0 to 2 | 1 | --- | F39 | 0=OFF
| 12DD | Switch Input B Trigger | 0 to 2 | 1 | --- | F39 | 0=OFF
| 12DE | Switch Input C Trigger | 0 to 2 | 1 | --- | F39 | 0=OFF
| 12DF | Switch Input D Trigger | 0 to 2 | 1 | --- | F39 | 0=OFF
| 12E0 | Trace Memory Trigger Delay | 0 to 30 | 1 | cycles | F1 | 0 cycles
| 12E1 | Trace Memory Waveform Selection | 0 to 6 | 1 | --- | F40 | 0=Ia
| 12E2 | Trace Memory Trigger Relay | 0 to 4 | 1 | --- | F29 | 0=OFF
| 12E3 | Reserved
| to |  |  |  |  |  | 
| 12EF | Reserved
PRODUCT OPTIONS | 12F0 | Product Options Upgrade | 1 to 23 | 1 | --- | F116 | 1=PQMII
| 12F1 | Product Modifications Upgrade MOD1 | 0 to 999 | 1 | --- | F1 | 0
| 12F2 | Product Modifications Upgrade MOD2 | 0 to 999 | 1 | --- | F1 | 0
| 12F3 | Product Modifications Upgrade MOD3 | 0 to 999 | 1 | --- | F1 | 0
| 12F4 | Product Modifications Upgrade MOD4 | 0 to 999 | 1 | --- | F1 | 0
| 12F5 | Product Modifications Upgrade MOD5 | 0 to 999 | 1 | --- | F1 | 0
| 12F6 | Passcode Input 1 | 32 to 127 | 1 | --- | F10 | 32
| 12F7 | Passcode Input 2 | 32 to 127 | 1 | --- | F10 | 32
| 12F8 | Passcode Input 3 | 32 to 127 | 1 | --- | F10 | 32
| 12F9 | Passcode Input 4 | 32 to 127 | 1 | --- | F10 | 32
PRODUCT OPTIONS continued | 12FA | Passcode Input 5 | 32 to 127 | 1 | --- | F10 | 32
| 12FB | Passcode Input 6 | 32 to 127 | 1 | --- | F10 | 32
| 12FC | Passcode Input 7 | 32 to 127 | 1 | --- | F10 | 32
| 12FD | Passcode Input 8 | 32 to 127 | 1 | --- | F10 | 32
| 12FE | Passcode Input 9 | 32 to 127 | 1 | --- | F10 | 32
| 12FF | Passcode Input 10 | 32 to 127 | 1 | --- | F10 | 32
| 1300 | Reserved
| to |  |  |  |  |  | 
| 131F | Reserved
VOLTAGE DISTUR- BANCE RECORDER | 1320 | Record Selector | 0 to 65535 | 1 | --- | F1 | 0
| 1321 | Sag Level % Nominal | 20 to 100 | 1 | % | F1*** | OFF
| 1322 | Swell Level % Nominal | 101 to 151 | 1 | % | F1*** | OFF
| 1323 | Reserved
| to |  |  |  |  |  | 
| 132F | Reserved
Notes: *Data type depends on the Command Operation Code. ** Any valid Actual Values or Setpoints address. *** Maximum Setpoint value represents “OFF”. **** Minimum Setpoint value represents “OFF”. ***** Maximum Setpoint value represents “UNLIMITED”.

## PQMII Data Formats
Code | Description | Bitmask
F1 | Unsigned Integer - Numerical Data | FFFF
F2 | Signed Integer - Numerical Data | FFFF
F3 | Unsigned Long Integer - Numerical Data | FFFFFFFF
F4 | Signed Long Integer - Numerical Data | FFFFFFFF
F5 | Hardware Version Code | FFFF
| 1 = A | ---
| 2 = B | ---
|  | 
| 26 = Z | ---
F6 | Unsigned Integer - Current Key Press | FFFF
| 0000 = no key | ---
| FE01 = Enter | ---
| FE02 = Menu | ---
| FE04 = Message Right | ---
| FE08 = Value Up | ---
| FD01 = Reset | ---
| FD02 = Message Left | ---
| FD04 = Message Up | ---
| FD08 = Value Down | ---
| FB01 = Escape | ---
| FB02 = Message Down | ---
F7 | Unsigned Integer - Command | FFFF
| 1 = Reset | ---
| 2 = Alarm Relay On | ---
| 3 = Alarm Relay Off | ---
| 4 = Auxiliary Relay 1 On | ---
| 5 = Auxiliary Relay 1 Off | ---
| 6 = Auxiliary Relay 2 On | ---
| 7 = Auxiliary Relay 2 Off | ---
| 8 = Auxiliary Relay 3 On | ---
| 9 = Auxiliary Relay 3 Off | ---
| 10 = Set Clock Time | ---
| 11 = Set Clock Date | ---
| 12 = Display 40 char. Flash Msg for 5 s | ---
| 13 = Simulate Keypress | ---
| 14 = Clear Energy Values | ---
| 15 = Clear Max. Demand Values | ---
| 16 = Clear Min./Max. Current Values | ---
| 17 = Clear Min./Max. Voltage Values | ---
| 18 = Clear Min./Max. Power Values | ---
| 19 = Clear Max. THD Values | ---
| 20 = Clear Switch Input Pulse Count | ---
| 21 = High Speed Sampling Trigger | ---
| 22 = Upload Mode Entry 2 | ---
| 23 = Upload Mode Entry 1 | ---
| 24 = Factory Setpoints Reload 2 | ---
| 25 = Factory Setpoints Reload 1 | ---
| 26 = Test Relays and LEDs | ---
| 27 = Waveform Capture Trigger | ---
| 28 = Start Data Log(s) | ---
| 29 = Stop Data Log(s) | ---
| 30 = Resize Data Logs (valid only if both logs are stopped) | ---
| 31 = Clear Event Record | ---
| 32= Trigger Trace Memory | ---
| 33= Re-arm Trace Mem. | ---
| 34= Clear All Demand | ---
| 35= Clear Min./Max. Freq | ---
| 40 = Clear Voltage Disturbance Recorder | ----
F8 | Unsigned Integer - Keypress Simulation | FFFF
| 49 = '1' = Menu | ---
| 50 = '2' = Escape | ---
| 51 = '3' = Reset | ---
| 52 = '4' = Enter | ---
| 53 = '5' = Message Up | ---
| 54 = '6' = Message Down | ---
| 55 = '7' = Message Left | ---
| 56 = '8' = Message Right | ---
| 57 = '9' = Value Up | ---
| 97 = 'a' = Value Down | ---
F9 | Unsigned Integer - Relay/LED Test Data | FFFF
| Alarm Relay | 1
| Auxiliary Relay 1 | 2
| Auxiliary Relay 2 | 4
| Auxiliary Relay 3 | 8
| ‘Alarm’ LED | 10
| ‘Program’ LED | 20
| ‘Simulation’ LED | 40
| ‘Self Test’ LED | 80
| ‘Alarm’ Relay LED | 100
| ‘Aux 1’ Relay LED | 200
| ‘Aux 2’ Relay LED | 400
| ‘Aux 3’ Relay LED | 800
F10 | Two ASCII Characters | FFFF
| 32-127 = ASCII Character | 7F00
| 32-127 = ASCII Character | 007F
F11 | Unsigned Integer - Enable/Disable | FFFF
| 0 = Disable/OFF | ---
| 1 = Enable/ON | ---
F12 | Unsigned Integer - Modbus Baud Rate | FFFF
| 0 = 1200 | ---
| 1 = 2400 | ---
| 2 = 4800 | ---
| 3 = 9600 | ---
| 4 = 19200 | ---
F13 | Unsigned Integer - Parity Type | FFFF
| 0 = None | ---
| 1 = Even | ---
| 2 = Odd | ---
F14 | UNSIGNED INTEGER - ANALOG OUTPUT TYPE | FFFF
| 0 = Not Used | ---
| 1 = Phase A Current | ---
| 2 = Phase B Current | ---
| 3 = Phase C Current | ---
| 4 = Neutral Current | ---
| 5 = Avg Phase Current | ---
| 6 = Current Unbalance | ---
| 7 = Voltage Van | ---
| 8 = Voltage Vbn | ---
| 9 = Voltage Vcn | ---
| 10 = Voltage Vab | ---
| 11 = Voltage Vbc | ---
| 12 = Voltage Vca | ---
| 13 = Avg Phase Voltage | ---
| 14 = Average Line Voltage | ---
| 15 = Voltage Unbalance | ---
| 16 = Frequency | ---
| 17 = 3 Power Factor | ---
| 18 = 3 Real Power (kW) | ---
| 19 = 3 Reactive Pwr (kvar) | ---
| 20 = 3 Apparent Pwr (kVA) | ---
| 21 = 3 Real Power (MW) | ---
| 22 = 3 Reactive Power (Mvar) | ---
| 23 = 3 Apparent Pwr (MVA) | ---
| 24 = Ph A Power Factor | ---
| 25 = Phase A Real Power | ---
| 26 = Ph A Reactive Power | ---
| 27 = Ph A Apparent Power | ---
| 28 = Ph B Power Factor | ---
| 29 = Phase B Real Power | ---
| 30 = Ph B Reactive Power | ---
| 31 = Ph B Apparent Power | ---
| 32 = Ph C Power Factor | ---
| 33 = Phase C Real Power | ---
| 34 = Ph C Reactive Power | ---
| 35 = Ph C Apparent Power | ---
| 36 = 3 Positive Real Energy Used | ---
| 37 = 3Positive Reactive Energy Used | ---
| 38 = 3 Negative Real Energy Used | ---
| 39 = 3 Negative Reactive Energy Used | ---
| 40 = 3 Apparent Energy Used | ---
| 41 = Ph A Current Dmd | ---
| 42 = Ph B Current Dmd | ---
| 43 = Ph C Current Dmd | ---
| 44 = Neutral Current Dmd | ---
| 45 = 3 Real Power Dmd | ---
| 46 = 3 Reactive Power Demand | ---
| 47 = 3 Apparent Power Demand | ---
| 48 = 3 Current THD | ---
| 49 = 3 Voltage THD | ---
| 50 = Phase A Current THD | ---
| 51 = Phase B Current THD | ---
| 52 = Phase C Current THD | ---
| 53 = Voltage Van THD | ---
| 54 = Voltage Vbn THD | ---
| 55 = Voltage Vcn THD | ---
| 56 = Voltage Vab THD | ---
| 57 = Voltage Vbc THD | ---
| 58 = Neutral Current THD | ---
| 59 = Serial Control | ---
F15 | Unsigned Integer - VT Wiring | FFFF
| 0 = Off | ---
| 1 = 4 Wire Wye / 3 VTs | ---
| 2 = 4 Wire Wye Direct | ---
| 3 = 4 Wire Wye / 2 VTs | ---
| 4 = 3 Wire Delta / 2 VTs | ---
| 5 = 3 Wire Direct | ---
| 6 = Single Phase Direct | ---
F16 | Unsigned Integer - Neutral Current Sensing | FFFF
| 0 = Off | ---
| 1 = Separate CT | ---
| 2 = Calculated | ---
F17 | Unsigned Integer -Failsafe/Non-failsafe | FFFF
| 0 =Non-failsafe | ---
| 1 = Failsafe | ---
F18 | Unsigned Integer - Unlatched / Latched | FFFF
| 0 = Unlatched | ---
| 1 = Latched | ---
F19 | Unsigned Integer - Aux Relay Function | FFFF
| 0 = Off | ---
| 1 = Aux1 Relay | ---
| 2 = Aux2 Relay | ---
| 3 = Aux3 Relay | ---
F20 | Unsigned Integer - Switch Function | FFFF
| 0 = Not Used | ---
| 1 = Alarm Relay | ---
| 2 = Auxiliary Relay 1 | ---
| 3 = Auxiliary Relay 2 | ---
| 4 = Auxiliary Relay 3 | ---
| 5 = Pulse Input 1 | ---
| 6 = New Demand Period | ---
| 7 = Setpoint Access | ---
| 8 = Select Main/Alt Analog Output | ---
| 9 = Select Main/Alt Analog Input | ---
| 10 = Pulse Input 2 | ---
| 11 = Pulse Input 3 | ---
| 12 = Pulse Input 4 | ---
| 13 = Clear Energy | ---
| 14 = Clear Demand | ---
F22 | Time Hours/minutes | FFFF
| Hours: 0 = 12 am, 1 = 1 am,..., 23 = 11 pm | FF00
| Minutes: 0 to 59 in steps of 1 | 00FF
F23 | Unsigned Integer - Time Seconds | FFFF
| Seconds: 0 = 0.000s,..., 59999 = 59.999s | ---
F24 | Date Month/day | FFFF
| Month: 1=January,..., 12=December | FF00
| Day: 1 to 31 in steps of 1 | 00FF
F25 | Unsigned Integer - Date Year | FFFF
| Year: 1995, 1996,... | ---
F26 | Unsigned Integer: Harmonic Spectrum Parameter | FFFF
| 0 = None | ---
| 1 = Phase A Current | ---
| 2 = Phase B Current | ---
| 3 = Phase C Current | ---
| 4 = Neutral Current | ---
| 5 = Voltage Vax | ---
| 6 = Voltage Vbx | ---
| 7 = Voltage Vcx | ---
F27 | Unsigned Integer - Switch Activation | FFFF
| 0 = Open | ---
| 1 = Closed | ---
F28 | Unsigned Integer: Demand Calculation | FFFF
| 0 = Thermal Exponential | ---
| 1 = Block Interval | ---
| 2 = Rolling Interval | ---
F29 | Unsigned Integer: Alarm/Control Relay | FFFF
| 0 = Off | ---
| 1 = Alarm Relay | ---
| 2 = Auxiliary Relay 1 | ---
| 3 = Auxiliary Relay 2 | ---
| 4 = Auxiliary Relay 3 | ---
F30 | Unsigned Integer: Phases Required | FFFF
| 0 = Any One | ---
| 1 = Any Two | ---
| 2 = All Three | ---
F31 | Unsigned Integer: Yes/No | FFFF
| 0 = No | ---
| 1 = Yes | ---
F32 | Unsigned Integer: Data Log Mode | FFFF
| 0 = Run to Fill | ---
| 1 = Circulate | ---
F33 | Unsigned Integer: Data Log Size Determination | FFFF
| 0 = Automatic | ---
| 1 = From Setpoint | ---
F34 | Unsigned Integer: Data Log Selection | FFFF
| 0 = None | ---
| 1 = Log 1 | ---
| 2 = Log 2 | ---
| 3 = Log 1 and Log 2 | ---
F35 | Unsigned Integer: Data Log Status | FFFF
| 0 = Stopped | ---
| 1 = Running | ---
F36 | Unsigned Integer: Cause Of Event | FFFF
| 0 = No Event | ---
| 1 = Clear Event Record | ---
| 2 = Power On | ---
| 3 = Power Off | ---
| 4 = Reset | ---
| 5 = Setpt Access Enabled | ---
| 6 = Switch A Alarm | ---
| 7 = Switch B Alarm | ---
| 8 = Switch C Alarm | ---
| 9 = Switch D Alarm | ---
| 10 = COM1 Fail Alarm | ---
| 11 = COM2 Fail Alarm | ---
| 12 = Self Test Alarm | ---
| 13 = Clock Not Set Alarm | ---
| 14 = Params Not Set Alrm | ---
| 15 = Underfreq Alarm | ---
| 16 = Overfreq Alarm | ---
| 17 = Undercurrent Alarm | ---
| 18 = Overcurrent Alarm | ---
| 19 = Neutral O/C Alarm | ---
| 20 = Undervoltage Alarm | ---
| 21 = Overvoltage Alarm | ---
| 22 = I Unbalance Alarm | ---
| 23 = V Unbalance Alarm | ---
| 24 = Phase Rev Alarm | ---
| 25 = PF Lead 1 Alarm | ---
| 26 = PF Lead 2 Alarm | ---
| 27 = PF Lag 1 Alarm | ---
| 28 = PF Lag 2 Alarm | ---
| 29 = Positive kW Alarm | ---
| 30 = Negative kW Alarm | ---
| 31 = Positive kvar Alarm | ---
| 32 = Negative kvar Alarm | ---
| 33 = +kW Demand Alarm | ---
| 34 = +kvar Dmd Alarm | ---
| 35 = –kW Demand Alarm | ---
| 36 = –kvar Dmd Alarm | ---
| 37 = kVA Demand Alarm | ---
| 38 = Phase A Current Demand Alarm | ---
| 39 = Phase B Current Demand Alarm | ---
| 40 = Phase C Current Demand Alarm | ---
| 41 = Neutral Current Demand Alarm | ---
| 42 = Pulse Input 1 Alarm | ---
| 43 = Current THD Alarm | ---
| 44 = Voltage THD Alarm | ---
| 45 = Analog In Main Alm | ---
| 46 = Analog In Alt Alarm | ---
| 47 = Data Log 1 Alarm | ---
| 48 = Data Log 2 Alarm | ---
| 49 = Switch A Alarm Clear | ---
| 50 = Switch B Alarm Clear | ---
| 51 = Switch C Alarm Clear | ---
| 52 = Switch D Alarm Clear | ---
| 53 = COM1 Fail Alarm Clr | ---
| 54 = COM2 Fail Alarm Clr | ---
| 55 = Self Test Alarm Clear | ---
| 56 = Clock Not Set Alarm Clear | ---
| 57 = Parameters Not Set Alarm Clear | ---
| 58 = Underfreq Alarm Clr | ---
| 59 = Overfreq Alarm Clear | ---
| 60 = U/C Alarm Clear | ---
| 61 = O/C Alarm Clear | ---
| 62 = Neutral Overcurrent Alarm Clear | ---
| 63 = U/V Alarm Clear | ---
| 64 = O/V Alarm Clear | ---
| 65 = Current Unbalance Alarm Clear | ---
| 66 = Voltage Unbalance Alarm Clear | ---
| 67 = Phase Reversal Alarm Clear | ---
| 68 = PF Lead 1 Alarm Clr | ---
| 69 = PF Lead 2 Alarm Clr | ---
| 70 = PF Lag 1 Alarm Clear | ---
| 71 = PF Lag 2 Alarm Clear | ---
| 72 = +kW Alarm Clear | ---
| 73 = –kW Alarm Clear | ---
| 74 = +kvar Alarm Clear | ---
| 75 = –kvar Alarm Clear | ---
| 76 = +kW Demand Alarm Clear | ---
| 77 = +kvar Demand Alarm Clear | ---
| 78 = –kW Demand Alarm Clear | ---
| 79 = –kvar Demand Alarm Clear | ---
| 80 = kVA Demand Alarm Clear | ---
| 81 = Phase A Current Demand Alarm Clear | ---
| 82 = Phase B Current Demand Alarm Clear | ---
| 83 = Phase C Current Demand Alarm Clear | ---
| 84 = Neutral Current Demand Alarm Clear | ---
| 85 = Pulse In 1 Alarm Clr | ---
| 86 = I THD Alarm Clear | ---
| 87 = V THD Alarm Clear | ---
| 88 = Analog Input Main Alarm Clear | ---
| 89 = Analog Input Alternate Alarm Clear | ---
| 90 = Data Log 1 Alarm Clr | ---
| 91 = Data Log 2 Alarm Clr | ---
| 92 = Pulse Input 2 Alarm | ---
| 93 = Pulse Input 3 Alarm | ---
| 94 = Pulse Input 4 Alarm | ---
| 95 = Pulse Count Total Alarm | ---
| 96 = Pulse In 2 Alarm Clr | ---
| 97 = Pulse In 3 Alarm Clr | ---
| 98 = Pulse In 4 Alarm Clr | ---
| 99 = Pulse Input Total Alarm Clear | ---
| 100 = Time Alarm | ---
| 101 = Time Alarm Clear | ---
| 102 = Trace Memory Trig | ---
F37 | Trace Memory Usage | FFFF
| 0 = 1 x 36 cycles | ---
| 1 = 2 x 18 cycles | ---
| 2 = 3 x 12 cycles | ---
F38 | Trace Memory Trigger Mode | FFFF
| 0 = One Shot | ---
| 1 = Retrigger | ---
F39 | Trace Memory Switch Input Trigger | FFFF
| 0 = Off | ---
| 1 = Open-to-closed | ---
| 2 = Closed-to-open | ---
F40 | Trace Memory Waveform Selection | FFFF
| 0 = Ia | ---
| 1 = Ib | ---
| 2 = Ic | ---
| 3 = In | ---
| 4 = Va | ---
| 5 = Vb | ---
| 6 = Vc | ---
F41 | Trace Memory Triggers | FFFF
| 0 = Trace Memory Not Triggered | ---
| 1 = Ia Overcurrent | ---
| 2 = Ib Overcurrent | ---
| 3 = Ic Overcurrent | ---
| 4 = In Overcurrent | ---
| 5 = Va Overvoltage | ---
| 6 = Vb Overvoltage | ---
| 7 = Vc Overvoltage | ---
| 8 = Va Undervoltage | ---
| 9 = Vb Undervoltage | ---
| 10 = Vc Undervoltage | ---
| 11 = Switch Input A | ---
| 12 = Switch Input B | ---
| 13 = Switch Input C | ---
| 14 = Switch Input D | ---
| 15 = Serial Comms. | ---
F43 | Pulse Input Totalization | FFFF
| 0 = 1+2 | ---
| 1 = 1+3 | ---
| 2 = 1+4 | ---
| 3 = 2+3 | ---
| 4 = 2+4 | ---
| 5 = 3+4 | ---
| 6 = 1+2+3 | ---
| 7 = 1+3+4 | ---
| 8 = 2+3+4 | ---
| 9 = 1+2+3+4 | ---
| 10 = 1+2+4 | ---
F44 | Phase CT Wiring | FFFF
| 0 = Phase A, B and C | ---
| 1 = Phase A and B only | ---
| 2 = Phase A and C only | ---
| 3 = Phase A only | ---
F45 | CPU Speed | FFFF
| 0 = 16 MHz | ---
| 1 = 25 MHz | ---
F47 | DNP Port | FFFF
| 0 = None | ---
| 1 = RS232 | ---
| 2 = COM1 | ---
| 3 = COM2 | ---
F100 | PQMII Options | FFFF
| PQMII (Display Version) | 1
| T20 (4-20mA Transducer) | 2
| T1 (0-1mA Transducer) | 4
| C (Control) Option | 8
| A (Power Analysis) Option | 10
F101 | Switch Input Status (0 = Open, 1 = Closed) | FFFF
| Switch A | 100
| Switch B | 200
| Switch C | 400
| Switch D | 800
F102 | LED Status Flags: (0=Inactive, 1=Active) | FFFF
| Aux 1 Relay | 1
| Aux 2 Relay | 2
| Aux 3 Relay | 4
| Alarm | 8
| Program | 10
| Simulation | 20
| Alarm Relay | 40
| Self Test | 80
F103 | LED Attribute Flags (0 = Flashing, 1 = Solid; Active) | FFFF
| Aux 1 Relay | 1
| Aux 2 Relay | 2
| Aux 3 Relay | 4
| Alarm | 8
| Program | 10
| Simulation | 20
| Alarm Relay | 40
| Self Test | 80
F104 | Output Relay Flag (0=de-energized, 1=energized) | FFFF
| Alarm Relay | 1
| Auxiliary Relay 1 | 2
| Auxiliary Relay 2 | 4
| Auxiliary Relay 3 | 8
F105 | Alarm Status Flags 1 | FFFF
| Phase Undercurrent Alarm | 1
| Phase Overcurrent Alarm | 2
| Neutral Overcurrent Alarm | 4
| Undervoltage Alarm | 8
| Overvoltage Alarm | 10
| Current Unbalance Alarm | 20
| Voltage Unbalance Alarm | 40
| Voltage Phase Reversal | 80
| PF Lead Alarm 1 | 100
| PF Lead Alarm 2 | 200
| Power Factor Lag Alarm 1 | 400
| Power Factor Lag Alarm 2 | 800
| Positive Real Power Alarm | 1000
| Neg Real Power Alarm | 2000
| Pos Reactive Power Alarm | 4000
| Neg Reactive Power Alarm | 8000
F106 | Alarm Status Flags 2 | FFFF
| Underfrequency Alarm | 1
| Overfrequency Alarm | 2
| Positive Real Power Demand Alarm | 4
| Positive Reactive Power Demand Alarm | 8
| Apparent Power Demand Alarm | 10
| Ph A Current Dmd Alarm | 20
| Ph B Current Dmd Alarm | 40
| Ph C Current Dmd Alarm | 80
| Neutral Current Demand Alarm | 100
| Switch A Alarm | 200
| Switch B Alarm | 400
| Switch C Alarm | 800
| Switch D Alarm | 1000
| Internal Fault Alarm | 2000
| Serial COM1 Failure Alarm | 4000
| Serial COM2 Failure Alarm | 8000
F107 | Alarm Status Flags 3 | FFFF
| Clock Not Set Alarm | 1
| Parameters Not Set Alarm | 2
| Pulse Input 1 Alarm | 4
| Current THD Alarm | 8
| Voltage THD Alarm | 10
| Analog Input Main Alarm | 20
| Analog Input Alt Alarm | 40
| Data Log 1 | 80
| Data Log 2 | 100
| Negative Real Power Demand Alarm | 200
| Negative Reactive Power Demand Alarm | 400
| Pulse Input 2 Alarm | 800
| Pulse Input 3 Alarm | 1000
| Pulse Input 4 Alarm | 2000
| Totalized Pulse In Alarm | 4000
| Time Alarm | 8000
F108 | Internal Fault Error Code | FFFF
| ADC Ref Out of Range | 1
| Reserved | 2
| Switch Input Circuit Fault | 4
| Reserved | 8
F109 | General Status | FFFF
| Alarm Present | 1
| Clock Not Set | 2
| Clock Drifting | 4
| Data Log 1 Running | 8
| Data Log 2 Running | 10
F110 | Data Logger Numbers | FFFF
| Log 1 | 1
| Log 2 | 2
F111 | Event Record Switches And Relay Status | FFFF
| Alarm Relay | 1
| Auxiliary Relay 1 | 2
| Auxiliary Relay 2 | 4
| Auxiliary Relay 3 | 8
F112 | Event Recorder Event Enable Flags 4 | FFFF
| Power On | 1
| Power Off | 2
| Alarm / Control Reset | 4
| Setpoint Access Enable | 8
F113 | Trace Memory Triggered Flag Status | FFFF
| 0 = Trace Memory Not Triggered | ---
| 1 = Trace Memory Triggered | ---
2 to 16 = Not Used
F114 | Power Alarms Level Base Units | FFFF
| 0 = kW/kVAR | ---
| 1 = MW/MVAR | ---
| 2 to 16 = Not Used | ---
F115 | Phase Overcurrent Activation | FFFF
| 0 = Average | ---
| 1 = Maximum | ---
| 2 to 16 = Not Used | ---
F116 | Product Options Upgrade | FFFF
| 1=PQMII | ---
| 3=PQMII-T20 | ---
| 5=PQMII-T1 | ---
| 7=PQMII-C | ---
| 9=PQMII-T20-C | ---
| 11=PQMII-T1-C | ---
| 13=PQMII-A | ---
| 15=PQMII-T20-A | ---
F116 ctd. | 17=PQMII-T1-A | ---
| 19=PQMII-C-A | ---
| 21=PQMII-T20-C-A | ---
| 23=PQMII-T1-C-A | ---
F117 | Invalid Serial Number Flag | FFFF
| 0=Serial Number Valid | ---
| 1= Serial Number Invalid | ---
F118 | Voltage Disturbance Type | FFFF
| Sag | 1
| Swell | 2
| Undervoltage | 4
| Overvoltage | 8
F119 | Voltage Disturbance Source | FFFF
| Voltage Van | 1
| Voltage Vbn | 2
| Voltage Vcn | 4
| Voltage Vab | 8
| Reserved | 10
| Voltage Vca | 20